## Summary Hours
Table of Motor Operating Hours by Building Type and Motor Use
Appendix E of the PA TRM
Building Type | Motor Usage Group | Motor Operating Hours
Office - Large | Chilled Water Pump | 1610
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 1610
| HVAC Fan | 4414.4
| Cooling Tower Fan | 1032
Office - Small | Chilled Water Pump | 1375
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 1375
| HVAC Fan | 3998.4
| Cooling Tower Fan | 1032
Hospitals & Healthcare - Pumps | Chilled Water Pump | 3801
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 3801
| HVAC Fan | -
| Cooling Tower Fan | -
Hospitals & Healthcare - HVAC | Chilled Water Pump | -
| Heating Hot Water Pump | -
| Condenser Water Pump | -
| HVAC Fan | 7243.2
| Cooling Tower Fan | 1032
Education - K-12 | Chilled Water Pump | 1444
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 1444
| HVAC Fan | 4164.8
| Cooling Tower Fan | 1032
Education - College & University | Chilled Water Pump | 1718
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 1718
| HVAC Fan | 4580.8
| Cooling Tower Fan | 1032
Retail | Chilled Water Pump | 2347
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 2347
| HVAC Fan | 5537.6
| Cooling Tower Fan | 1032
Restaurants - Fast Food | Chilled Water Pump | 2901
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 2901
| HVAC Fan | 6702.4
| Cooling Tower Fan | 1032
Restaurants - Sit Down | Chilled Water Pump | 2160
| Heating Hot Water Pump | 4959
| Condenser Water Pump | 2160
| HVAC Fan | 5246.4
| Cooling Tower Fan | 1032
CALCULATION METHOD
Motor Usage Group | Method of Operating Hours Calculation
Chilled Water Pump | Hours when ambient temperature is above 60°F during building operating hours
Heating Hot Water Pump | Hours when ambient temperature is below 60°F during all hours
Condenser Water Pump | Hours when ambient temperature is above 60°F during building operating hours
HVAC Fan | Operating hours and 20% of unoccupied hours
Cooling Tower Fan | Cooling EFLH according to EPA 2002 (1032 hours for Philadelphia)
NOTES
1. Ambient temperature is derived from BIN Master weather data from Philadelphia.
2. Operating hours for each building type is estimated for typical use from Hours Worksheet
3. Hospital & Healthcare operating hours differ for pumps and HVAC.

## Hours Worksheet
Worksheet for Table of Motor Hours of Operation by Building Type and Motor Function
Appendix E of the PA TRM
|  | Weekdays Operating Hrs |  |  | Weekends Operating Hrs |  |  | Total Bldg Operating Hrs | Bldg Hrs/Total Hrs |  | Motor Operating
BIN # | Building Type | Open | Close | Hours | Open | Close | Hours | Hours | Ratio | Motor Usage Group | Hours
1 | Total Hours | 0 | 24 | 24 | 0 | 24 | 24 | 8760 | 1 | Chilled Water Pump | 3801
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 3801
[10 empty] | HVAC Fan | 8760
[10 empty] | Cooling Tower Fan | 1032
2 | Office - Large | 8 | 20 | 12 | 8 | 10 | 2 | 3328 | 0.37991 | Chilled Water Pump | 1610
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 1610
[10 empty] | HVAC Fan | 4414.4
[10 empty] | Cooling Tower Fan | 1032
3 | Office - Small | 8 | 18 | 10 | 8 | 10 | 2 | 2808 | 0.32055 | Chilled Water Pump | 1375
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 1375
[10 empty] | HVAC Fan | 3998.4
[10 empty] | Cooling Tower Fan | 1032
4 | Hospitals & Healthcare - Pumps | 0 | 24 | 24 | 0 | 24 | 24 | 8760 | 1 | Chilled Water Pump | 3801
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 3801
[10 empty] | HVAC Fan | -
[10 empty] | Cooling Tower Fan | -
5 | Hospitals & Healthcare - HVAC | 6 | 2 | 20 | 8 | 24 | 16 | 6864 | 0.78356 | Chilled Water Pump | -
[10 empty] | Heating Hot Water Pump | -
[10 empty] | Condenser Water Pump | -
[10 empty] | HVAC Fan | 7243.2
[10 empty] | Cooling Tower Fan | 1032
6 | Education - K-12 | 7 | 17 | 10 | 8 | 12 | 4 | 3016 | 0.34429 | Chilled Water Pump | 1444
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 1444
[10 empty] | HVAC Fan | 4164.8
[10 empty] | Cooling Tower Fan | 1032
7 | Education - College & University | 8 | 20 | 12 | 8 | 12 | 4 | 3536 | 0.40365 | Chilled Water Pump | 1718
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 1718
[10 empty] | HVAC Fan | 4580.8
[10 empty] | Cooling Tower Fan | 1032
8 | Retail | 9 | 22 | 13 | 9 | 22 | 13 | 4732 | 0.54018 | Chilled Water Pump | 2347
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 2347
[10 empty] | HVAC Fan | 5537.6
[10 empty] | Cooling Tower Fan | 1032
9 | Restaurants - Fast Food | 6 | 23 | 17 | 6 | 23 | 17 | 6188 | 0.70639 | Chilled Water Pump | 2901
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 2901
[10 empty] | HVAC Fan | 6702.4
[10 empty] | Cooling Tower Fan | 1032
10 | Restaurants - Sit Down | 11 | 23 | 12 | 11 | 23 | 12 | 4368 | 0.49863 | Chilled Water Pump | 2160
[10 empty] | Heating Hot Water Pump | 4959
[10 empty] | Condenser Water Pump | 2160
[10 empty] | HVAC Fan | 5246.4
[10 empty] | Cooling Tower Fan | 1032
| Type | Method of Hours Calculation
| Chilled Water Pump | Hours when Ambient Temperature is above 60, during operating hours
| Heating Hot Water Pump | Hours when Ambient Temperature is below 60, during all hours
| Condenser Water Pump | Hours when Ambient Temperature is above 60, during operating hours
| HVAC Fan | Operating hours + 20% of unoccupied hours
| Cooling Tower Fan | EFLH of cooling hours (select location below)
| LOCATION | EFLH
| Philadelphia | 1032
| Allentown | 784
| Erie | 482
| Harrisburg | 929
| Philadelphia | 1032
| Pittsburgh | 737
| Scranton | 621
| Williamsport | 659
EFLH values taken from: http://www.energystar.gov/ia/business/bulk_purchasing/bpsavings_calc/Calc_CAC.xls

## BIN1
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 8760
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 2 | 2 | 2 | 2 | 2 | 2
3 | 3 | 3 | 3 | 3 | 3 | 3
4 | 4 | 4 | 4 | 4 | 4 | 4
5 | 5 | 5 | 5 | 5 | 5 | 5
6 | 6 | 6 | 6 | 6 | 6 | 6
7 | 7 | 7 | 7 | 7 | 7 | 7
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
12 | 12 | 12 | 12 | 12 | 12 | 12
13 | 13 | 13 | 13 | 13 | 13 | 13
14 | 14 | 14 | 14 | 14 | 14 | 14
15 | 15 | 15 | 15 | 15 | 15 | 15
16 | 16 | 16 | 16 | 16 | 16 | 16
17 | 17 | 17 | 17 | 17 | 17 | 17
18 | 18 | 18 | 18 | 18 | 18 | 18
19 | 19 | 19 | 19 | 19 | 19 | 19
20 | 20 | 20 | 20 | 20 | 20 | 20
21 | 21 | 21 | 21 | 21 | 21 | 21
22 | 22 | 22 | 22 | 22 | 22 | 22
23 | 23 | 23 | 23 | 23 | 23 | 23
24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
97.5 | 95 to 100 | 3 | 24 July: 3 | 95 to 100 | 3 | 3 | 0 | 100% | 3 | 0% | 0
92.5 | 90 to 95 | 52 | 24 June: 11; 24 July: 30; 24 August: 11 | 90 to 95 | 52 | 52 | 0 | 88.57% | 46.0571 | 0% | 0
87.5 | 85 to 90 | 104 | 24 June: 34; 24 July: 53; 24 August: 15; 24 September: 2 | 85 to 90 | 104 | 104 | 0 | 77.14% | 80.2286 | 0% | 0
82.5 | 80 to 85 | 477 | 24 April: 6; 24 May: 13; 24 June: 86; 24 July: 184; 24 August: 132; 24 September: 52; 24 October: 4 | 80 to 85 | 477 | 477 | 0 | 65.71% | 313.4571 | 0% | 0
77.5 | 75 to 80 | 656 |  |  |  | 2 | 68 | 97 | 198 | 168 | 96 | 17 | 10 |  | 75 to 80 | 656 | 656 | 0 | 54.29% | 356.1143 | 0% | 0
72.5 | 70 to 75 | 907 |  |  |  | 24 | 100 | 161 | 161 | 198 | 200 | 52 | 11 |  | 70 to 75 | 907 | 907 | 0 | 42.86% | 388.7143 | 0% | 0
67.5 | 65 to 70 | 619 |  |  |  | 23 | 96 | 117 | 62 | 137 | 96 | 78 | 10 |  | 65 to 70 | 619 | 619 | 0 | 31.43% | 194.5429 | 0% | 0
62.5 | 60 to 65 | 983 |  |  | 21 | 72 | 203 | 179 | 52 | 79 | 165 | 145 | 66 | 1 | 60 to 65 | 983 | 983 | 0 | 20% | 196.6 | 0% | 0
57.5 | 55 to 60 | 625 |  |  | 53 | 118 | 123 | 29 | 1 | 4 | 91 | 102 | 96 | 8 | 55 to 60 | 625 | 0 | 625 | 0% | 0 | 20% | 125
52.5 | 50 to 55 | 540 |  | 19 | 66 | 115 | 89 | 5 |  |  | 13 | 127 | 93 | 13 | 50 to 55 | 540 | 0 | 540 | 0% | 0 | 28.89% | 156
47.5 | 45 to 50 | 576 | 21 | 22 | 122 | 187 | 36 | 1 |  |  | 5 | 80 | 66 | 36 | 45 to 50 | 576 | 0 | 576 | 0% | 0 | 37.78% | 217.6
42.5 | 40 to 45 | 552 | 86 | 38 | 113 | 97 | 15 |  |  |  |  | 51 | 75 | 77 | 40 to 45 | 552 | 0 | 552 | 0% | 0 | 46.67% | 257.6
37.5 | 35 to 40 | 1067 | 142 | 197 | 196 | 61 | 1 |  |  |  |  | 65 | 148 | 257 | 35 to 40 | 1067 | 0 | 1067 | 0% | 0 | 55.56% | 592.7778
32.5 | 30 to 35 | 685 | 24 January: 119; 24 February: 155; 24 March: 105; 24 April: 15; 24 October: 17; 24 November: 106; 24 December: 168 | 30 to 35 | 685 | 0 | 685 | 0% | 0 | 64.44% | 441.4444
27.5 | 25 to 30 | 442 | 24 January: 153; 24 February: 73; 24 March: 56; 24 October: 6; 24 November: 35; 24 December: 119 | 25 to 30 | 442 | 0 | 442 | 0% | 0 | 73.33% | 324.1333
22.5 | 20 to 25 | 248 | 24 January: 101; 24 February: 92; 24 March: 12; 24 November: 4; 24 December: 39 | 20 to 25 | 248 | 0 | 248 | 0% | 0 | 82.22% | 203.9111
17.5 | 15 to 20 | 184 | 24 January: 98; 24 February: 60; 24 December: 26 | 15 to 20 | 184 | 0 | 184 | 0% | 0 | 91.11% | 167.6444
12.5 | 10 to 15 | 40 | 24 January: 24; 24 February: 16 | 10 to 15 | 40 | 0 | 40 | 0% | 0 | 100% | 40
[15 empty] | TOTAL | 8760 | 3801 | 4959 |  | 1578.7143 |  | 2526.1111

## BIN2
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 3330
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
| 10 | 10 | 10 | 10 | 10
| 11 | 11 | 11 | 11 | 11
| 12 | 12 | 12 | 12 | 12
| 13 | 13 | 13 | 13 | 13
| 14 | 14 | 14 | 14 | 14
| 15 | 15 | 15 | 15 | 15
| 16 | 16 | 16 | 16 | 16
| 17 | 17 | 17 | 17 | 17
| 18 | 18 | 18 | 18 | 18
| 19 | 19 | 19 | 19 | 19
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs
92.5 | 90 to 95 | 34 | 19 June: 9; 19 July: 14; 19 August: 11 | 90 to 95 | 34 | 34 | 0
87.5 | 85 to 90 | 85 | 19 June: 30; 19 July: 38; 19 August: 15; 19 September: 2 | 85 to 90 | 85 | 85 | 0
82.5 | 80 to 85 | 305 | 19 May: 8; 19 June: 67; 19 July: 122; 19 August: 75; 19 September: 29; 19 October: 4 | 80 to 85 | 305 | 305 | 0
77.5 | 75 to 80 | 305 | 19 May: 29; 19 June: 43; 19 July: 62; 19 August: 92; 19 September: 62; 19 October: 15; 19 November: 2 | 75 to 80 | 305 | 305 | 0
72.5 | 70 to 75 | 357 |  |  |  | 15 | 60 | 74 | 29 | 68 | 85 | 22 | 4 |  | 70 to 75 | 357 | 357 | 0
67.5 | 65 to 70 | 211 |  |  |  | 15 | 48 | 31 | 4 | 27 | 30 | 51 | 5 |  | 65 to 70 | 211 | 211 | 0
62.5 | 60 to 65 | 313 |  |  | 9 | 30 | 77 | 26 | 3 | 4 | 54 | 75 | 35 |  | 60 to 65 | 313 | 313 | 0
57.5 | 55 to 60 | 219 | 19 March: 39; 19 April: 49; 19 May: 44; 19 September: 8; 19 October: 43; 19 November: 36 | 55 to 60 | 219 | 0 | 219
52.5 | 50 to 55 | 191 | 19 February: 18; 19 March: 25; 19 April: 50; 19 May: 24; 19 October: 25; 19 November: 48; 19 December: 1 | 50 to 55 | 191 | 0 | 191
47.5 | 45 to 50 | 224 | 11 | 14 | 62 | 67 | 2 |  |  |  |  | 21 | 33 | 14 | 45 to 50 | 224 | 0 | 224
42.5 | 40 to 45 | 250 | 19 January: 46; 19 February: 23; 19 March: 51; 19 April: 27; 19 October: 18; 19 November: 41; 19 December: 44 | 40 to 45 | 250 | 0 | 250
37.5 | 35 to 40 | 355 | 19 January: 57; 19 February: 60; 19 March: 64; 19 April: 7; 19 October: 8; 19 November: 53; 19 December: 106 | 35 to 40 | 355 | 0 | 355
32.5 | 30 to 35 | 212 | 19 January: 52; 19 February: 54; 19 March: 32; 19 November: 20; 19 December: 54 | 30 to 35 | 212 | 0 | 212
27.5 | 25 to 30 | 136 | 19 January: 55; 19 February: 32; 19 March: 9; 19 November: 3; 19 December: 37 | 25 to 30 | 136 | 0 | 136
22.5 | 20 to 25 | 91 | 19 January: 40; 19 February: 37; 19 March: 1; 19 December: 13 | 20 to 25 | 91 | 0 | 91
17.5 | 15 to 20 | 38 | 19 January: 18; 19 February: 17; 19 December: 3 | 15 to 20 | 38 | 0 | 38
12.5 | 10 to 15 | 4 | 19 January: 3; 19 February: 1 | 10 to 15 | 4 | 0 | 4
[15 empty] | 0 | 0 | 0 | 0
[15 empty] | TOTAL | 3330 | 1610 | 1720

## BIN3
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 2810
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
| 10 | 10 | 10 | 10 | 10
| 11 | 11 | 11 | 11 | 11
| 12 | 12 | 12 | 12 | 12
| 13 | 13 | 13 | 13 | 13
| 14 | 14 | 14 | 14 | 14
| 15 | 15 | 15 | 15 | 15
| 16 | 16 | 16 | 16 | 16
| 17 | 17 | 17 | 17 | 17
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
92.5 | 90 to 95 | 31 | 17 June: 7; 17 July: 13; 17 August: 11 | 90 to 95 | 31 | 31 | 0 | 100% | 31 | 0% | 0
87.5 | 85 to 90 | 77 | 17 June: 30; 17 July: 33; 17 August: 12; 17 September: 2 | 85 to 90 | 77 | 77 | 0 | 86.67% | 66.7333 | 0% | 0
82.5 | 80 to 85 | 264 | 17 May: 8; 17 June: 51; 17 July: 101; 17 August: 71; 17 September: 29; 17 October: 4 | 80 to 85 | 264 | 264 | 0 | 73.33% | 193.6 | 0% | 0
77.5 | 75 to 80 | 255 | 17 May: 25; 17 June: 38; 17 July: 49; 17 August: 72; 17 September: 54; 17 October: 15; 17 November: 2 | 75 to 80 | 255 | 255 | 0 | 60% | 153 | 0% | 0
72.5 | 70 to 75 | 302 |  |  |  | 13 | 51 | 64 | 29 | 55 | 70 | 16 | 4 |  | 70 to 75 | 302 | 302 | 0 | 46.67% | 140.9333 | 0% | 0
67.5 | 65 to 70 | 174 |  |  |  | 13 | 40 | 23 | 4 | 21 | 23 | 46 | 4 |  | 65 to 70 | 174 | 174 | 0 | 33.33% | 58 | 0% | 0
62.5 | 60 to 65 | 272 |  |  | 9 | 26 | 65 | 23 | 1 | 4 | 43 | 67 | 34 |  | 60 to 65 | 272 | 272 | 0 | 20% | 54.4 | 0% | 0
57.5 | 55 to 60 | 181 | 17 March: 33; 17 April: 40; 17 May: 36; 17 September: 7; 17 October: 35; 17 November: 30 | 55 to 60 | 181 | 0 | 181 | 0% | 0 | 20% | 36.2
52.5 | 50 to 55 | 154 | 17 February: 15; 17 March: 21; 17 April: 40; 17 May: 20; 17 October: 16; 17 November: 41; 17 December: 1 | 50 to 55 | 154 | 0 | 154 | 0% | 0 | 28.89% | 44.4889
47.5 | 45 to 50 | 192 | 11 | 11 | 52 | 58 | 1 |  |  |  |  | 19 | 26 | 14 | 45 to 50 | 192 | 0 | 192 | 0% | 0 | 37.78% | 72.5333
42.5 | 40 to 45 | 212 | 17 January: 39; 17 February: 21; 17 March: 44; 17 April: 23; 17 October: 14; 17 November: 34; 17 December: 37 | 40 to 45 | 212 | 0 | 212 | 0% | 0 | 46.67% | 98.9333
37.5 | 35 to 40 | 291 | 17 January: 46; 17 February: 48; 17 March: 51; 17 April: 7; 17 October: 6; 17 November: 44; 17 December: 89 | 35 to 40 | 291 | 0 | 291 | 0% | 0 | 55.56% | 161.6667
32.5 | 30 to 35 | 177 | 17 January: 44; 17 February: 48; 17 March: 27; 17 November: 14; 17 December: 44 | 30 to 35 | 177 | 0 | 177 | 0% | 0 | 64.44% | 114.0667
27.5 | 25 to 30 | 121 | 17 January: 50; 17 February: 27; 17 March: 8; 17 November: 3; 17 December: 33 | 25 to 30 | 121 | 0 | 121 | 0% | 0 | 73.33% | 88.7333
22.5 | 20 to 25 | 67 | 17 January: 29; 17 February: 28; 17 March: 1; 17 December: 9 | 20 to 25 | 67 | 0 | 67 | 0% | 0 | 82.22% | 55.0889
17.5 | 15 to 20 | 36 | 17 January: 16; 17 February: 17; 17 December: 3 | 15 to 20 | 36 | 0 | 36 | 0% | 0 | 91.11% | 32.8
12.5 | 10 to 15 | 4 | 17 January: 3; 17 February: 1 | 10 to 15 | 4 | 0 | 4 | 0% | 0 | 100% | 4
[15 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 100% | 0
[15 empty] | TOTAL | 2810 | 1375 | 1435 |  | 697.6667 |  | 708.5111

## BIN4
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 8760
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 2 | 2 | 2 | 2 | 2 | 2
3 | 3 | 3 | 3 | 3 | 3 | 3
4 | 4 | 4 | 4 | 4 | 4 | 4
5 | 5 | 5 | 5 | 5 | 5 | 5
6 | 6 | 6 | 6 | 6 | 6 | 6
7 | 7 | 7 | 7 | 7 | 7 | 7
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
12 | 12 | 12 | 12 | 12 | 12 | 12
13 | 13 | 13 | 13 | 13 | 13 | 13
14 | 14 | 14 | 14 | 14 | 14 | 14
15 | 15 | 15 | 15 | 15 | 15 | 15
16 | 16 | 16 | 16 | 16 | 16 | 16
17 | 17 | 17 | 17 | 17 | 17 | 17
18 | 18 | 18 | 18 | 18 | 18 | 18
19 | 19 | 19 | 19 | 19 | 19 | 19
20 | 20 | 20 | 20 | 20 | 20 | 20
21 | 21 | 21 | 21 | 21 | 21 | 21
22 | 22 | 22 | 22 | 22 | 22 | 22
23 | 23 | 23 | 23 | 23 | 23 | 23
24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
97.5 | 95 to 100 | 3 | 24 July: 3 | 95 to 100 | 3 | 3 | 0 | 100% | 3 | 0% | 0
92.5 | 90 to 95 | 52 | 24 June: 11; 24 July: 30; 24 August: 11 | 90 to 95 | 52 | 52 | 0 | 88.57% | 46.0571 | 0% | 0
87.5 | 85 to 90 | 104 | 24 June: 34; 24 July: 53; 24 August: 15; 24 September: 2 | 85 to 90 | 104 | 104 | 0 | 77.14% | 80.2286 | 0% | 0
82.5 | 80 to 85 | 477 | 24 April: 6; 24 May: 13; 24 June: 86; 24 July: 184; 24 August: 132; 24 September: 52; 24 October: 4 | 80 to 85 | 477 | 477 | 0 | 65.71% | 313.4571 | 0% | 0
77.5 | 75 to 80 | 656 |  |  |  | 2 | 68 | 97 | 198 | 168 | 96 | 17 | 10 |  | 75 to 80 | 656 | 656 | 0 | 54.29% | 356.1143 | 0% | 0
72.5 | 70 to 75 | 907 |  |  |  | 24 | 100 | 161 | 161 | 198 | 200 | 52 | 11 |  | 70 to 75 | 907 | 907 | 0 | 42.86% | 388.7143 | 0% | 0
67.5 | 65 to 70 | 619 |  |  |  | 23 | 96 | 117 | 62 | 137 | 96 | 78 | 10 |  | 65 to 70 | 619 | 619 | 0 | 31.43% | 194.5429 | 0% | 0
62.5 | 60 to 65 | 983 |  |  | 21 | 72 | 203 | 179 | 52 | 79 | 165 | 145 | 66 | 1 | 60 to 65 | 983 | 983 | 0 | 20% | 196.6 | 0% | 0
57.5 | 55 to 60 | 625 |  |  | 53 | 118 | 123 | 29 | 1 | 4 | 91 | 102 | 96 | 8 | 55 to 60 | 625 | 0 | 625 | 0% | 0 | 20% | 125
52.5 | 50 to 55 | 540 |  | 19 | 66 | 115 | 89 | 5 |  |  | 13 | 127 | 93 | 13 | 50 to 55 | 540 | 0 | 540 | 0% | 0 | 28.89% | 156
47.5 | 45 to 50 | 576 | 21 | 22 | 122 | 187 | 36 | 1 |  |  | 5 | 80 | 66 | 36 | 45 to 50 | 576 | 0 | 576 | 0% | 0 | 37.78% | 217.6
42.5 | 40 to 45 | 552 | 86 | 38 | 113 | 97 | 15 |  |  |  |  | 51 | 75 | 77 | 40 to 45 | 552 | 0 | 552 | 0% | 0 | 46.67% | 257.6
37.5 | 35 to 40 | 1067 | 142 | 197 | 196 | 61 | 1 |  |  |  |  | 65 | 148 | 257 | 35 to 40 | 1067 | 0 | 1067 | 0% | 0 | 55.56% | 592.7778
32.5 | 30 to 35 | 685 | 24 January: 119; 24 February: 155; 24 March: 105; 24 April: 15; 24 October: 17; 24 November: 106; 24 December: 168 | 30 to 35 | 685 | 0 | 685 | 0% | 0 | 64.44% | 441.4444
27.5 | 25 to 30 | 442 | 24 January: 153; 24 February: 73; 24 March: 56; 24 October: 6; 24 November: 35; 24 December: 119 | 25 to 30 | 442 | 0 | 442 | 0% | 0 | 73.33% | 324.1333
22.5 | 20 to 25 | 248 | 24 January: 101; 24 February: 92; 24 March: 12; 24 November: 4; 24 December: 39 | 20 to 25 | 248 | 0 | 248 | 0% | 0 | 82.22% | 203.9111
17.5 | 15 to 20 | 184 | 24 January: 98; 24 February: 60; 24 December: 26 | 15 to 20 | 184 | 0 | 184 | 0% | 0 | 91.11% | 167.6444
12.5 | 10 to 15 | 40 | 24 January: 24; 24 February: 16 | 10 to 15 | 40 | 0 | 40 | 0% | 0 | 100% | 40
[15 empty] | TOTAL | 8760 | 3801 | 4959 |  | 1578.7143 |  | 2526.1111

## BIN5
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 6985
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
| 1 | 1 | 1 | 1 | 1
| 6 | 6 | 6 | 6 | 6
| 7 | 7 | 7 | 7 | 7
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
12 | 12 | 12 | 12 | 12 | 12 | 12
13 | 13 | 13 | 13 | 13 | 13 | 13
14 | 14 | 14 | 14 | 14 | 14 | 14
15 | 15 | 15 | 15 | 15 | 15 | 15
16 | 16 | 16 | 16 | 16 | 16 | 16
17 | 17 | 17 | 17 | 17 | 17 | 17
18 | 18 | 18 | 18 | 18 | 18 | 18
19 | 19 | 19 | 19 | 19 | 19 | 19
20 | 20 | 20 | 20 | 20 | 20 | 20
21 | 21 | 21 | 21 | 21 | 21 | 21
22 | 22 | 22 | 22 | 22 | 22 | 22
23 | 23 | 23 | 23 | 23 | 23 | 23
24 | 24 | 24 | 24 | 24 | 24 | 24
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
97.5 | 95 to 100 | 3 | 24 July: 3 | 95 to 100 | 3 | 3 | 0 | 100% | 3 | 0% | 0
92.5 | 90 to 95 | 52 | 24 June: 11; 24 July: 30; 24 August: 11 | 90 to 95 | 52 | 52 | 0 | 88.57% | 46.0571 | 0% | 0
87.5 | 85 to 90 | 104 | 24 June: 34; 24 July: 53; 24 August: 15; 24 September: 2 | 85 to 90 | 104 | 104 | 0 | 77.14% | 80.2286 | 0% | 0
82.5 | 80 to 85 | 476 | 24 April: 6; 24 May: 13; 24 June: 86; 24 July: 183; 24 August: 132; 24 September: 52; 24 October: 4 | 80 to 85 | 476 | 476 | 0 | 65.71% | 312.8 | 0% | 0
77.5 | 75 to 80 | 602 |  |  |  | 2 | 68 | 93 | 158 | 158 | 96 | 17 | 10 |  | 75 to 80 | 602 | 602 | 0 | 54.29% | 326.8 | 0% | 0
72.5 | 70 to 75 | 746 |  |  |  | 24 | 98 | 136 | 108 | 149 | 172 | 48 | 11 |  | 70 to 75 | 746 | 746 | 0 | 42.86% | 319.7143 | 0% | 0
67.5 | 65 to 70 | 478 |  |  |  | 23 | 85 | 97 | 31 | 95 | 65 | 72 | 10 |  | 65 to 70 | 478 | 478 | 0 | 31.43% | 150.2286 | 0% | 0
62.5 | 60 to 65 | 732 |  |  | 21 | 72 | 161 | 110 | 24 | 35 | 131 | 125 | 52 | 1 | 60 to 65 | 732 | 732 | 0 | 20% | 146.4 | 0% | 0
57.5 | 55 to 60 | 460 |  |  | 53 | 101 | 84 | 7 |  | 1 | 46 | 82 | 79 | 7 | 55 to 60 | 460 | 0 | 460 | 0% | 0 | 20% | 92
52.5 | 50 to 55 | 433 |  | 19 | 60 | 98 | 62 | 2 |  |  | 7 | 99 | 79 | 7 | 50 to 55 | 433 | 0 | 433 | 0% | 0 | 28.89% | 125.0889
47.5 | 45 to 50 | 464 | 19 | 22 | 107 | 146 | 20 |  |  |  | 2 | 52 | 61 | 35 | 45 to 50 | 464 | 0 | 464 | 0% | 0 | 37.78% | 175.2889
42.5 | 40 to 45 | 456 | 77 | 38 | 96 | 60 | 5 |  |  |  |  | 43 | 70 | 67 | 40 to 45 | 456 | 0 | 456 | 0% | 0 | 46.67% | 212.8
37.5 | 35 to 40 | 822 | 24 January: 117; 24 February: 149; 24 March: 140; 24 April: 33; 24 October: 43; 24 November: 118; 24 December: 222 | 35 to 40 | 822 | 0 | 822 | 0% | 0 | 55.56% | 456.6667
32.5 | 30 to 35 | 513 | 24 January: 103; 24 February: 126; 24 March: 79; 24 April: 5; 24 October: 6; 24 November: 68; 24 December: 126 | 30 to 35 | 513 | 0 | 513 | 0% | 0 | 64.44% | 330.6
27.5 | 25 to 30 | 311 | 24 January: 113; 24 February: 64; 24 March: 31; 24 October: 2; 24 November: 17; 24 December: 84 | 25 to 30 | 311 | 0 | 311 | 0% | 0 | 73.33% | 228.0667
22.5 | 20 to 25 | 183 | 24 January: 79; 24 February: 68; 24 March: 9; 24 November: 1; 24 December: 26 | 20 to 25 | 183 | 0 | 183 | 0% | 0 | 82.22% | 150.4667
17.5 | 15 to 20 | 127 | 24 January: 69; 24 February: 43; 24 December: 15 | 15 to 20 | 127 | 0 | 127 | 0% | 0 | 91.11% | 115.7111
12.5 | 10 to 15 | 23 | 24 January: 16; 24 February: 7 | 10 to 15 | 23 | 0 | 23 | 0% | 0 | 100% | 23
[15 empty] | TOTAL | 6985 | 3193 | 3792 |  | 1385.2286 |  | 1909.6889

## BIN6
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 3020
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
| 7 | 7 | 7 | 7 | 7
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
| 12 | 12 | 12 | 12 | 12
| 13 | 13 | 13 | 13 | 13
| 14 | 14 | 14 | 14 | 14
| 15 | 15 | 15 | 15 | 15
| 16 | 16 | 16 | 16 | 16
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
92.5 | 90 to 95 | 28 | 16 June: 6; 16 July: 12; 16 August: 10 | 90 to 95 | 28 | 28 | 0 | 100% | 28 | 0% | 0
87.5 | 85 to 90 | 72 | 16 June: 24; 16 July: 35; 16 August: 11; 16 September: 2 | 85 to 90 | 72 | 72 | 0 | 86.67% | 62.4 | 0% | 0
82.5 | 80 to 85 | 256 | 16 May: 8; 16 June: 53; 16 July: 95; 16 August: 67; 16 September: 29; 16 October: 4 | 80 to 85 | 256 | 256 | 0 | 73.33% | 187.7333 | 0% | 0
77.5 | 75 to 80 | 269 |  |  |  | 1 | 24 | 39 | 61 | 78 | 52 | 12 | 2 |  | 75 to 80 | 269 | 269 | 0 | 60% | 161.4 | 0% | 0
72.5 | 70 to 75 | 326 |  |  |  | 11 | 57 | 65 | 36 | 59 | 73 | 18 | 7 |  | 70 to 75 | 326 | 326 | 0 | 46.67% | 152.1333 | 0% | 0
67.5 | 65 to 70 | 207 |  |  |  | 14 | 41 | 32 | 10 | 30 | 28 | 48 | 4 |  | 65 to 70 | 207 | 207 | 0 | 33.33% | 69 | 0% | 0
62.5 | 60 to 65 | 286 |  |  | 7 | 26 | 64 | 32 | 1 | 7 | 48 | 68 | 33 |  | 60 to 65 | 286 | 286 | 0 | 20% | 57.2 | 0% | 0
57.5 | 55 to 60 | 189 | 16 March: 31; 16 April: 42; 16 May: 41; 16 June: 1; 16 September: 12; 16 October: 34; 16 November: 28 | 55 to 60 | 189 | 0 | 189 | 0% | 0 | 20% | 37.8
52.5 | 50 to 55 | 173 |  | 13 | 22 | 43 | 23 |  |  |  | 1 | 23 | 45 | 3 | 50 to 55 | 173 | 0 | 173 | 0% | 0 | 28.89% | 49.9778
47.5 | 45 to 50 | 210 | 12 | 11 | 53 | 65 | 4 |  |  |  | 1 | 21 | 26 | 17 | 45 to 50 | 210 | 0 | 210 | 0% | 0 | 37.78% | 79.3333
42.5 | 40 to 45 | 218 | 16 January: 36; 16 February: 21; 16 March: 48; 16 April: 24; 16 October: 16; 16 November: 36; 16 December: 37 | 40 to 45 | 218 | 0 | 218 | 0% | 0 | 46.67% | 101.7333
37.5 | 35 to 40 | 309 | 16 January: 48; 16 February: 53; 16 March: 52; 16 April: 13; 16 October: 10; 16 November: 43; 16 December: 90 | 35 to 40 | 309 | 0 | 309 | 0% | 0 | 55.56% | 171.6667
32.5 | 30 to 35 | 210 | 16 January: 49; 16 February: 54; 16 March: 33; 16 April: 1; 16 October: 1; 16 November: 21; 16 December: 51 | 30 to 35 | 210 | 0 | 210 | 0% | 0 | 64.44% | 135.3333
27.5 | 25 to 30 | 132 | 16 January: 49; 16 February: 26; 16 March: 11; 16 October: 1; 16 November: 7; 16 December: 38 | 25 to 30 | 132 | 0 | 132 | 0% | 0 | 73.33% | 96.8
22.5 | 20 to 25 | 74 | 16 January: 31; 16 February: 30; 16 March: 5; 16 December: 8 | 20 to 25 | 74 | 0 | 74 | 0% | 0 | 82.22% | 60.8444
17.5 | 15 to 20 | 52 | 16 January: 26; 16 February: 20; 16 December: 6 | 15 to 20 | 52 | 0 | 52 | 0% | 0 | 91.11% | 47.3778
12.5 | 10 to 15 | 9 | 16 January: 5; 16 February: 4 | 10 to 15 | 9 | 0 | 9 | 0% | 0 | 100% | 9
[15 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 100% | 0
[15 empty] | TOTAL | 3020 | 1444 | 1576 |  | 717.8667 |  | 789.8667

## BIN7
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 3540
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
| 12 | 12 | 12 | 12 | 12
| 13 | 13 | 13 | 13 | 13
| 14 | 14 | 14 | 14 | 14
| 15 | 15 | 15 | 15 | 15
| 16 | 16 | 16 | 16 | 16
| 17 | 17 | 17 | 17 | 17
| 18 | 18 | 18 | 18 | 18
| 19 | 19 | 19 | 19 | 19
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
92.5 | 90 to 95 | 35 | 19 June: 9; 19 July: 15; 19 August: 11 | 90 to 95 | 35 | 35 | 0 | 100% | 35 | 0% | 0
87.5 | 85 to 90 | 91 | 19 June: 30; 19 July: 44; 19 August: 15; 19 September: 2 | 85 to 90 | 91 | 91 | 0 | 86.67% | 78.8667 | 0% | 0
82.5 | 80 to 85 | 322 | 19 May: 8; 19 June: 73; 19 July: 127; 19 August: 78; 19 September: 32; 19 October: 4 | 80 to 85 | 322 | 322 | 0 | 73.33% | 236.1333 | 0% | 0
77.5 | 75 to 80 | 333 |  |  |  | 1 | 32 | 44 | 68 | 105 | 66 | 15 | 2 |  | 75 to 80 | 333 | 333 | 0 | 60% | 199.8 | 0% | 0
72.5 | 70 to 75 | 384 |  |  |  | 16 | 68 | 78 | 31 | 68 | 92 | 24 | 7 |  | 70 to 75 | 384 | 384 | 0 | 46.67% | 179.2 | 0% | 0
67.5 | 65 to 70 | 228 |  |  |  | 16 | 52 | 34 | 4 | 27 | 32 | 57 | 6 |  | 65 to 70 | 228 | 228 | 0 | 33.33% | 76 | 0% | 0
62.5 | 60 to 65 | 325 |  |  | 9 | 33 | 78 | 28 | 3 | 4 | 56 | 79 | 35 |  | 60 to 65 | 325 | 325 | 0 | 20% | 65 | 0% | 0
57.5 | 55 to 60 | 225 | 19 March: 40; 19 April: 53; 19 May: 44; 19 September: 8; 19 October: 44; 19 November: 36 | 55 to 60 | 225 | 0 | 225 | 0% | 0 | 20% | 45
52.5 | 50 to 55 | 207 | 19 February: 18; 19 March: 28; 19 April: 56; 19 May: 24; 19 October: 28; 19 November: 50; 19 December: 3 | 50 to 55 | 207 | 0 | 207 | 0% | 0 | 28.89% | 59.8
47.5 | 45 to 50 | 241 | 11 | 14 | 67 | 71 | 2 |  |  |  |  | 22 | 37 | 17 | 45 to 50 | 241 | 0 | 241 | 0% | 0 | 37.78% | 91.0444
42.5 | 40 to 45 | 263 | 19 January: 46; 19 February: 25; 19 March: 56; 19 April: 27; 19 October: 19; 19 November: 43; 19 December: 47 | 40 to 45 | 263 | 0 | 263 | 0% | 0 | 46.67% | 122.7333
37.5 | 35 to 40 | 371 | 19 January: 62; 19 February: 65; 19 March: 64; 19 April: 7; 19 October: 8; 19 November: 56; 19 December: 109 | 35 to 40 | 371 | 0 | 371 | 0% | 0 | 55.56% | 206.1111
32.5 | 30 to 35 | 234 | 19 January: 57; 19 February: 60; 19 March: 34; 19 November: 21; 19 December: 62 | 30 to 35 | 234 | 0 | 234 | 0% | 0 | 64.44% | 150.8
27.5 | 25 to 30 | 141 | 19 January: 58; 19 February: 33; 19 March: 9; 19 November: 3; 19 December: 38 | 25 to 30 | 141 | 0 | 141 | 0% | 0 | 73.33% | 103.4
22.5 | 20 to 25 | 93 | 19 January: 41; 19 February: 38; 19 March: 1; 19 December: 13 | 20 to 25 | 93 | 0 | 93 | 0% | 0 | 82.22% | 76.4667
17.5 | 15 to 20 | 43 | 19 January: 22; 19 February: 18; 19 December: 3 | 15 to 20 | 43 | 0 | 43 | 0% | 0 | 91.11% | 39.1778
12.5 | 10 to 15 | 4 | 19 January: 3; 19 February: 1 | 10 to 15 | 4 | 0 | 4 | 0% | 0 | 100% | 4
[15 empty] | 0 | 0 | 0 | 0 | 0% | 0 | 100% | 0
[15 empty] | TOTAL | 3540 | 1718 | 1822 |  | 870 |  | 898.5333

## BIN8
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 4745
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
12 | 12 | 12 | 12 | 12 | 12 | 12
13 | 13 | 13 | 13 | 13 | 13 | 13
14 | 14 | 14 | 14 | 14 | 14 | 14
15 | 15 | 15 | 15 | 15 | 15 | 15
16 | 16 | 16 | 16 | 16 | 16 | 16
17 | 17 | 17 | 17 | 17 | 17 | 17
18 | 18 | 18 | 18 | 18 | 18 | 18
19 | 19 | 19 | 19 | 19 | 19 | 19
20 | 20 | 20 | 20 | 20 | 20 | 20
21 | 21 | 21 | 21 | 21 | 21 | 21
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
97.5 | 95 to 100 | 3 | 21 July: 3 | 95 to 100 | 3 | 3 | 0 | 100% | 3 | 0% | 0
92.5 | 90 to 95 | 52 | 21 June: 11; 21 July: 30; 21 August: 11 | 90 to 95 | 52 | 52 | 0 | 88.57% | 46.0571 | 0% | 0
87.5 | 85 to 90 | 104 | 21 June: 34; 21 July: 53; 21 August: 15; 21 September: 2 | 85 to 90 | 104 | 104 | 0 | 77.14% | 80.2286 | 0% | 0
82.5 | 80 to 85 | 460 | 21 April: 6; 21 May: 13; 21 June: 84; 21 July: 173; 21 August: 128; 21 September: 52; 21 October: 4 | 80 to 85 | 460 | 460 | 0 | 65.71% | 302.2857 | 0% | 0
77.5 | 75 to 80 | 491 |  |  |  | 2 | 68 | 72 | 96 | 132 | 94 | 17 | 10 |  | 75 to 80 | 491 | 491 | 0 | 54.29% | 266.5429 | 0% | 0
72.5 | 70 to 75 | 496 |  |  |  | 24 | 87 | 97 | 39 | 78 | 122 | 38 | 11 |  | 70 to 75 | 496 | 496 | 0 | 42.86% | 212.5714 | 0% | 0
67.5 | 65 to 70 | 297 |  |  |  | 23 | 61 | 56 | 4 | 35 | 43 | 65 | 10 |  | 65 to 70 | 297 | 297 | 0 | 31.43% | 93.3429 | 0% | 0
62.5 | 60 to 65 | 444 |  |  | 21 | 66 | 99 | 36 | 5 | 4 | 67 | 104 | 41 | 1 | 60 to 65 | 444 | 444 | 0 | 20% | 88.8 | 0% | 0
57.5 | 55 to 60 | 280 | 21 March: 49; 21 April: 68; 21 May: 42; 21 September: 9; 21 October: 57; 21 November: 51; 21 December: 4 | 55 to 60 | 280 | 0 | 280 | 0% | 0 | 20% | 56
52.5 | 50 to 55 | 297 |  | 18 | 51 | 84 | 29 |  |  |  | 1 | 52 | 56 | 6 | 50 to 55 | 297 | 0 | 297 | 0% | 0 | 28.89% | 85.8
47.5 | 45 to 50 | 335 | 15 | 22 | 92 | 86 | 4 |  |  |  |  | 31 | 54 | 31 | 45 to 50 | 335 | 0 | 335 | 0% | 0 | 37.78% | 126.5556
42.5 | 40 to 45 | 316 | 21 January: 56; 21 February: 32; 21 March: 63; 21 April: 27; 21 October: 25; 21 November: 55; 21 December: 58 | 40 to 45 | 316 | 0 | 316 | 0% | 0 | 46.67% | 147.4667
37.5 | 35 to 40 | 514 | 21 January: 92; 21 February: 99; 21 March: 75; 21 April: 4; 21 October: 10; 21 November: 77; 21 December: 157 | 35 to 40 | 514 | 0 | 514 | 0% | 0 | 55.56% | 285.5556
32.5 | 30 to 35 | 314 | 21 January: 76; 21 February: 82; 21 March: 43; 21 November: 25; 21 December: 88 | 30 to 35 | 314 | 0 | 314 | 0% | 0 | 64.44% | 202.3556
27.5 | 25 to 30 | 180 | 21 January: 79; 21 February: 49; 21 March: 9; 21 December: 43 | 25 to 30 | 180 | 0 | 180 | 0% | 0 | 73.33% | 132
22.5 | 20 to 25 | 116 | 21 January: 56; 21 February: 45; 21 December: 15 | 20 to 25 | 116 | 0 | 116 | 0% | 0 | 82.22% | 95.3778
17.5 | 15 to 20 | 40 | 21 January: 23; 21 February: 17 | 15 to 20 | 40 | 0 | 40 | 0% | 0 | 91.11% | 36.4444
12.5 | 10 to 15 | 6 | 21 January: 6 | 10 to 15 | 6 | 0 | 6 | 0% | 0 | 100% | 6
[15 empty] | TOTAL | 4745 | 2347 | 2398 |  | 1092.8286 |  | 1173.5556

## BIN9
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 6205
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
6 | 6 | 6 | 6 | 6 | 6 | 6
7 | 7 | 7 | 7 | 7 | 7 | 7
8 | 8 | 8 | 8 | 8 | 8 | 8
9 | 9 | 9 | 9 | 9 | 9 | 9
10 | 10 | 10 | 10 | 10 | 10 | 10
11 | 11 | 11 | 11 | 11 | 11 | 11
12 | 12 | 12 | 12 | 12 | 12 | 12
13 | 13 | 13 | 13 | 13 | 13 | 13
14 | 14 | 14 | 14 | 14 | 14 | 14
15 | 15 | 15 | 15 | 15 | 15 | 15
16 | 16 | 16 | 16 | 16 | 16 | 16
17 | 17 | 17 | 17 | 17 | 17 | 17
18 | 18 | 18 | 18 | 18 | 18 | 18
19 | 19 | 19 | 19 | 19 | 19 | 19
20 | 20 | 20 | 20 | 20 | 20 | 20
21 | 21 | 21 | 21 | 21 | 21 | 21
22 | 22 | 22 | 22 | 22 | 22 | 22
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
97.5 | 95 to 100 | 3 | 22 July: 3 | 95 to 100 | 3 | 3 | 0 | 100% | 3 | 0% | 0
92.5 | 90 to 95 | 52 | 22 June: 11; 22 July: 30; 22 August: 11 | 90 to 95 | 52 | 52 | 0 | 88.57% | 46.0571 | 0% | 0
87.5 | 85 to 90 | 104 | 22 June: 34; 22 July: 53; 22 August: 15; 22 September: 2 | 85 to 90 | 104 | 104 | 0 | 77.14% | 80.2286 | 0% | 0
82.5 | 80 to 85 | 475 | 22 April: 6; 22 May: 13; 22 June: 86; 22 July: 183; 22 August: 131; 22 September: 52; 22 October: 4 | 80 to 85 | 475 | 475 | 0 | 65.71% | 312.1429 | 0% | 0
77.5 | 75 to 80 | 562 |  |  |  | 2 | 68 | 85 | 137 | 148 | 95 | 17 | 10 |  | 75 to 80 | 562 | 562 | 0 | 54.29% | 305.0857 | 0% | 0
72.5 | 70 to 75 | 660 |  |  |  | 24 | 94 | 123 | 85 | 127 | 153 | 43 | 11 |  | 70 to 75 | 660 | 660 | 0 | 42.86% | 282.8571 | 0% | 0
67.5 | 65 to 70 | 416 |  |  |  | 23 | 78 | 82 | 22 | 72 | 60 | 69 | 10 |  | 65 to 70 | 416 | 416 | 0 | 31.43% | 130.7429 | 0% | 0
62.5 | 60 to 65 | 629 |  |  | 21 | 71 | 140 | 81 | 14 | 22 | 105 | 123 | 51 | 1 | 60 to 65 | 629 | 629 | 0 | 20% | 125.8 | 0% | 0
57.5 | 55 to 60 | 387 |  |  | 51 | 83 | 68 | 7 |  | 1 | 36 | 73 | 63 | 5 | 55 to 60 | 387 | 0 | 387 | 0% | 0 | 20% | 77.4
52.5 | 50 to 55 | 395 |  | 19 | 56 | 98 | 52 | 1 |  |  | 5 | 81 | 74 | 9 | 50 to 55 | 395 | 0 | 395 | 0% | 0 | 28.89% | 114.1111
47.5 | 45 to 50 | 417 | 18 | 22 | 101 | 126 | 12 |  |  |  | 2 | 45 | 57 | 34 | 45 to 50 | 417 | 0 | 417 | 0% | 0 | 37.78% | 157.5333
42.5 | 40 to 45 | 403 | 66 | 37 | 83 | 48 | 2 |  |  |  |  | 40 | 63 | 64 | 40 to 45 | 403 | 0 | 403 | 0% | 0 | 46.67% | 188.0667
37.5 | 35 to 40 | 707 | 22 January: 112; 22 February: 130; 22 March: 119; 22 April: 23; 22 October: 25; 22 November: 103; 22 December: 195 | 35 to 40 | 707 | 0 | 707 | 0% | 0 | 55.56% | 392.7778
32.5 | 30 to 35 | 439 | 22 January: 91; 22 February: 109; 22 March: 64; 22 April: 6; 22 October: 5; 22 November: 50; 22 December: 114 | 30 to 35 | 439 | 0 | 439 | 0% | 0 | 64.44% | 282.9111
27.5 | 25 to 30 | 272 | 22 January: 101; 22 February: 56; 22 March: 25; 22 October: 2; 22 November: 17; 22 December: 71 | 25 to 30 | 272 | 0 | 272 | 0% | 0 | 73.33% | 199.4667
22.5 | 20 to 25 | 168 | 22 January: 75; 22 February: 61; 22 March: 7; 22 November: 1; 22 December: 24 | 20 to 25 | 168 | 0 | 168 | 0% | 0 | 82.22% | 138.1333
17.5 | 15 to 20 | 94 | 22 January: 49; 22 February: 35; 22 December: 10 | 15 to 20 | 94 | 0 | 94 | 0% | 0 | 91.11% | 85.6444
12.5 | 10 to 15 | 22 | 22 January: 15; 22 February: 7 | 10 to 15 | 22 | 0 | 22 | 0% | 0 | 100% | 22
[15 empty] | TOTAL | 6205 | 2901 | 3304 |  | 1285.9143 |  | 1658.0444

## BIN10
Conventional Binning :
Units: | I-P | 13739 | PHILADELPHIA | N 39 53 | W 75 15 | 29.529 ft
Date: Dec 07,2009 | # hrs: 4380
Jan Feb Mar Apr May Jun Jul Aug Sep Oct Nov Dec
Sun | Mon | Tue | Wed | Thu | Fri | Sat
11 | 11 | 11 | 11 | 11 | 11 | 11
12 | 12 | 12 | 12 | 12 | 12 | 12
13 | 13 | 13 | 13 | 13 | 13 | 13
14 | 14 | 14 | 14 | 14 | 14 | 14
15 | 15 | 15 | 15 | 15 | 15 | 15
16 | 16 | 16 | 16 | 16 | 16 | 16
17 | 17 | 17 | 17 | 17 | 17 | 17
18 | 18 | 18 | 18 | 18 | 18 | 18
19 | 19 | 19 | 19 | 19 | 19 | 19
20 | 20 | 20 | 20 | 20 | 20 | 20
21 | 21 | 21 | 21 | 21 | 21 | 21
22 | 22 | 22 | 22 | 22 | 22 | 22
|  | Total | January | February | March | April | May | June | July | August | September | October | November | December |  | Total | Over 60 | Under 60 | Cooling | Cooling | Heating | Heating
Mid-pts | DB (F) | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | Hrs | DB (F) | Hrs | Hrs | Hrs | % | EFLH | % | EFLH
97.5 | 95 to 100 | 3 | 22 July: 3 | 95 to 100 | 3 | 3 | 0 | 100% | 3 | 0% | 0
92.5 | 90 to 95 | 52 | 22 June: 11; 22 July: 30; 22 August: 11 | 90 to 95 | 52 | 52 | 0 | 88.57% | 46.0571 | 0% | 0
87.5 | 85 to 90 | 96 | 22 June: 32; 22 July: 48; 22 August: 14; 22 September: 2 | 85 to 90 | 96 | 96 | 0 | 77.14% | 74.0571 | 0% | 0
82.5 | 80 to 85 | 425 | 22 April: 6; 22 May: 13; 22 June: 74; 22 July: 154; 22 August: 124; 22 September: 50; 22 October: 4 | 80 to 85 | 425 | 425 | 0 | 65.71% | 279.2857 | 0% | 0
77.5 | 75 to 80 | 436 |  |  |  | 2 | 65 | 64 | 84 | 110 | 85 | 16 | 10 |  | 75 to 80 | 436 | 436 | 0 | 54.29% | 236.6857 | 0% | 0
72.5 | 70 to 75 | 452 |  |  |  | 23 | 73 | 89 | 38 | 69 | 112 | 38 | 10 |  | 70 to 75 | 452 | 452 | 0 | 42.86% | 193.7143 | 0% | 0
67.5 | 65 to 70 | 269 |  |  |  | 22 | 55 | 50 | 9 | 39 | 32 | 54 | 8 |  | 65 to 70 | 269 | 269 | 0 | 31.43% | 84.5429 | 0% | 0
62.5 | 60 to 65 | 427 |  |  | 21 | 61 | 98 | 39 | 6 | 5 | 65 | 93 | 38 | 1 | 60 to 65 | 427 | 427 | 0 | 20% | 85.4 | 0% | 0
57.5 | 55 to 60 | 258 |  |  | 47 | 63 | 33 | 1 |  |  | 12 | 48 | 49 | 5 | 55 to 60 | 258 | 0 | 258 | 0% | 0 | 20% | 51.6
52.5 | 50 to 55 | 289 |  | 19 | 50 | 78 | 31 |  |  |  | 2 | 54 | 50 | 5 | 50 to 55 | 289 | 0 | 289 | 0% | 0 | 28.89% | 83.4889
47.5 | 45 to 50 | 299 | 13 | 20 | 77 | 78 | 4 |  |  |  |  | 29 | 49 | 29 | 45 to 50 | 299 | 0 | 299 | 0% | 0 | 37.78% | 112.9556
42.5 | 40 to 45 | 285 | 22 January: 55; 22 February: 29; 22 March: 56; 22 April: 23; 22 October: 25; 22 November: 48; 22 December: 49 | 40 to 45 | 285 | 0 | 285 | 0% | 0 | 46.67% | 133
37.5 | 35 to 40 | 499 | 22 January: 89; 22 February: 93; 22 March: 74; 22 April: 4; 22 October: 11; 22 November: 73; 22 December: 155 | 35 to 40 | 499 | 0 | 499 | 0% | 0 | 55.56% | 277.2222
32.5 | 30 to 35 | 285 | 22 January: 68; 22 February: 77; 22 March: 40; 22 November: 24; 22 December: 76 | 30 to 35 | 285 | 0 | 285 | 0% | 0 | 64.44% | 183.6667
27.5 | 25 to 30 | 164 | 22 January: 74; 22 February: 42; 22 March: 7; 22 November: 1; 22 December: 40 | 25 to 30 | 164 | 0 | 164 | 0% | 0 | 73.33% | 120.2667
22.5 | 20 to 25 | 105 | 22 January: 48; 22 February: 46; 22 December: 11 | 20 to 25 | 105 | 0 | 105 | 0% | 0 | 82.22% | 86.3333
17.5 | 15 to 20 | 30 | 22 January: 19; 22 February: 10; 22 December: 1 | 15 to 20 | 30 | 0 | 30 | 0% | 0 | 91.11% | 27.3333
12.5 | 10 to 15 | 6 | 22 January: 6 | 10 to 15 | 6 | 0 | 6 | 0% | 0 | 100% | 6
[15 empty] | TOTAL | 4380 | 2160 | 2220 |  | 1002.7429 |  | 1081.8667