## Manual
Pennsylvania Act 129 Motor & VFD Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Motor & VFD Audit and Design Tool is two-fold:
1. To document the pre- and post-installation cases.
2. To facilitate the calculation of energy savings and demand reduction for motor installations.
II. Organization
The Motor & VFD Audit and Design Tool is organized into 3 sheets.
(1) Manual
The "Manual" sheet contains the instruction manual for using the Motor & VFD Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) Motor & VFD Form
The "Motor & VFD Form" sheet contains the main worksheet that collects all relevant information to calculate energy savings and peak demand reduction. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes.
(4) Glossary
The "Glossary" sheet is a reference for the "Motor and VFD Form" sheet. It defines each of the columns for clarification.
III. User Guide
The tool contains all information regarding motors and VFDs required for the calculation of savings pursuant to the PA TRM. The use of this tool is encouraged but not required. Users of the Motor and VFD Audit and Design Tool must complete the "Motor and VFD Form". The designer must select the appropriate facility type and the utility from the drop down menu. Use one line on the pre-installation table and post-installation table for each unique motor, i.e. motors with different operating conditions or different motor specifications. Complete all yellow fields to calculate the peak demand reduction and annual energy savings. Pink fields are computed automatically. Roll mouse over the field heading for additional help. Projects within facility types or motor functions not included on the drop down menu must follow custom protocols to determine appropriate run hours and ESF/DSF values. Motor replacements with the following conditions should also follow custom protocols:
* Variable frequency drive (VFD) control on the existing (baseline) motor
* Two-speed motor (existing and/or new)
* Single speed motor with variable loading (not standard)
* Abnormal motor loading (i.e., load factor differs from 0.75)
* Industrial process applications
* Applications where the building type or motor usage group is not listed in Table 6-12 of the TRM
* New motor has a different rated horsepower than the existing motor
* Change in annual operating hours is anticipated
IV. Disclaimer
This document does not modify any requirements of the PA TRM and is provided for convenience only. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Changelog
Pennsylvania Act 129 Lighting Audit and Design Tool
CHANGELOG
Version 7 (Effective June 3, 2010)
1. Released with TRM Order in June 2010
Version 8 (Submitted October 27, 2011. Effective June 1, 2011)
1. Created Changelog
2. Revised "Manual" and "Glossary" to improve user guide and increase usability
3. Revised "Manual" and "Glossary" to reflect new changes to the TRM

## Motor and VFD Form
Motor and Variable Frequency Drive Inventory Form | [8 empty] | Appendix D of the PA TRM |  | Complete one copy of this form for each building with a motor or VFD measure
Applicant Name: | [6 empty] | Project Name:
Facility Name: | [6 empty] | Survey completed by (name):
Facility Type: |  | Office - Large |  |  |  |  | Spot Measurements completed by (name):
Utility: |  | Allegheny Power |  |  |  |  | Date(s) Survey completed:
Installation Date:
Pre-Installation Data (Equipment Survey of Existing Motors)
[7 empty] | Nameplate Data | [5 empty] | Pre-Installation Energy Consumption
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Motor Configuration | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | VFD |  |  | Total per Unit |  |  |  | Total all Units
[13 empty] | VFD on Motor | ESF | DSF | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh |  |  | Baseline Motor Efficiency | [6 empty] | Efficient Motor Efficiency | [6 empty] | Main Lookup Table
[42 empty] | ESF |  |  |  | DSF
ex. | CWP-1 | CWP | 2 | 0.75 | Single | 1 | Acme | 10000 | 50 | 1800 | ODP | 93% | No | 1 | 1 | 30.1 | 30.1 | 3801 | 114410 | 60.2 | 228820 | Facility Types |  | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | Facility | Motor Function | Concatenate | Run Hours | ESF | Zone 1 | Zone 2 | Zone 3 | DSF | Zone 1 | Zone 2 | Zone 3
[22 empty] | Office - Large |  | 1 | 80% | 82.5% | 75.5% | 80% | 82.5% | 75.5% | 1 | 82.5% | 85.5% | 77% | 82.5% | 85.5% | 77% | Office - Large | CHWP | Office - LargeCHWP | 1610 | 0.283 | 0.305 | 0.283 | 0.282 | 0.596 | 0.792 | 0.596 | 0.548
1 | [21 empty] | Office - Small |  | 1.5 | 84% | 84% | 82.5% | 85.5% | 84% | 82.5% | 1.5 | 86.5% | 86.5% | 84% | 87.5% | 86.5% | 84% | Office - Large | HWP | Office - LargeHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
2 | [21 empty] | Hospitals & Healthcare - Pumps |  | 2 | 85.5% | 84% | 84% | 86.5% | 84% | 84% | 2 | 87.5% | 86.5% | 85.5% | 88.5% | 86.5% | 85.5% | Office - Large | CWP | Office - LargeCWP | 1610 | 0.244 | 0.27 | 0.244 | 0.245 | 0.596 | 0.792 | 0.596 | 0.548
3 | [21 empty] | Hospitals & Healthcare - HVAC |  | 3 | 86.5% | 86.5% | 84% | 87.5% | 87.5% | 85.5% | 3 | 88.5% | 89.5% | 85.5% | 89.5% | 89.5% | 86.5% | Office - Large | HVACF | Office - LargeHVACF | 4414.4 | 0.278 | 0.293 | 0.278 | 0.276 | 0.694 | 0.849 | 0.694 | 0.657
4 | [21 empty] | Education - K-12 |  | 5 | 87.5% | 87.5% | 85.5% | 87.5% | 87.5% | 87.5% | 5 | 89.5% | 89.5% | 86.5% | 89.5% | 89.5% | 88.5% | Office - Large | CTF | Office - LargeCTF | 1032 | 0.244 | 0.27 | 0.244 | 0.245 | 0.596 | 0.792 | 0.596 | 0.548
5 | [21 empty] | Education - College & University |  | 7.5 | 88.5% | 88.5% | 87.5% | 89.5% | 89.5% | 88.5% | 7.5 | 90.2% | 91% | 88.5% | 91% | 91.7% | 89.5% | Office - Small | CHWP | Office - SmallCHWP | 1375 | 0.286 | 0.308 | 0.286 | 0.286 | 0.586 | 0.781 | 0.586 | 0.548
6 | [21 empty] | Retail |  | 10 | 90.2% | 89.5% | 88.5% | 89.5% | 89.5% | 89.5% | 10 | 91.7% | 91.7% | 89.5% | 91% | 91.7% | 90.2% | Office - Small | HWP | Office - SmallHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
7 | [21 empty] | Restaurants - Fast Food |  | 15 | 90.2% | 91% | 89.5% | 90.2% | 91% | 90.2% | 15 | 91.7% | 93% | 90.2% | 91.7% | 92.4% | 91% | Office - Small | CWP | Office - SmallCWP | 1375 | 0.246 | 0.273 | 0.246 | 0.248 | 0.586 | 0.781 | 0.586 | 0.548
8 | [21 empty] | Restaurants - Sit Down |  | 20 | 91% | 91% | 90.2% | 90.2% | 91% | 90.2% | 20 | 92.4% | 93% | 91% | 91.7% | 93% | 91% | Office - Small | HVACF | Office - SmallHVACF | 3998.4 | 0.279 | 0.295 | 0.279 | 0.278 | 0.686 | 0.841 | 0.686 | 0.657
9 | [23 empty] | 25 | 91.7% | 91.7% | 91% | 91.7% | 92.4% | 91% | 25 | 93% | 93.6% | 91.7% | 93% | 93.6% | 91.7% | Office - Small | CTF | Office - SmallCTF | 1032 | 0.246 | 0.273 | 0.246 | 0.248 | 0.586 | 0.781 | 0.586 | 0.548
10 | [21 empty] | Motor Functions |  | 30 | 92.4% | 92.4% | 91% | 91.7% | 92.4% | 91% | 30 | 93.6% | 94.1% | 91.7% | 93% | 93.6% | 91.7% | Hospitals & Healthcare - Pumps | CHWP | Hospitals & Healthcare - PumpsCHWP | 3801 | 0.262 | 0.275 | 0.262 | 0.257 | 0.675 | 0.869 | 0.675 | 0.594
[20 empty] | 0 | 0 | CHWP |  | 40 | 93% | 93% | 91.7% | 93% | 93% | 91.7% | 40 | 94.1% | 94.1% | 92.4% | 94.1% | 94.1% | 92.4% | Hospitals & Healthcare - Pumps | HWP | Hospitals & Healthcare - PumpsHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
Post-Installation Data (Equipment Survey of Proposed Motors) | [21 empty] | HWP |  | 50 | 93% | 93% | 92.4% | 93% | 93% | 92.4% | 50 | 94.1% | 94.5% | 93% | 94.1% | 94.5% | 93% | Hospitals & Healthcare - Pumps | CWP | Hospitals & Healthcare - PumpsCWP | 3801 | 0.211 | 0.231 | 0.211 | 0.206 | 0.75 | 0.869 | 0.75 | 0.594
[7 empty] | Nameplate Data | [5 empty] | Post-Installation Energy Consumption | [8 empty] | CWP |  | 60 | 93.6% | 93.6% | 93% | 93.6% | 93.6% | 93% | 60 | 94.5% | 95% | 93.6% | 94.5% | 95% | 93.6% | Hospitals & Healthcare - Pumps | HVACF | Hospitals & Healthcare - PumpsHVACF | - | - | - | - | - | - | - | - | -
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Motor Configuration | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | VFD |  |  | Total per Unit |  |  |  | Total all Units |  | HVACF |  | 75 | 93.6% | 94.1% | 93% | 93.6% | 94.1% | 93% | 75 | 94.5% | 95% | 93.6% | 94.5% | 95.4% | 93.6% | Hospitals & Healthcare - Pumps | CTF | Hospitals & Healthcare - PumpsCTF | - | - | - | - | - | - | - | - | -
[13 empty] | VFD on Motor | ESF | DSF | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh | CTF |  | 100 | 94.1% | 94.1% | 93% | 94.1% | 94.5% | 93.6% | 100 | 95% | 95.4% | 93.6% | 95% | 95.4% | 94.1% | Hospitals & Healthcare - HVAC | CHWP | Hospitals & Healthcare - HVACCHWP | - | - | - | - | - | - | - | - | -
[24 empty] | 125 | 94.1% | 94.5% | 93.6% | 94.1% | 94.5% | 94.5% | 125 | 95% | 95.4% | 94.1% | 95% | 95.4% | 95% | Hospitals & Healthcare - HVAC | HWP | Hospitals & Healthcare - HVACHWP | - | - | - | - | - | - | - | - | -
ex. | CWP-1 | CWP | 2 | 0.75 | Single | 1 | Acme | 20000 | 50 | 1800 | ODP | 94.5% | No | 1 | 1 | 29.6 | 29.6 | 3801 | 112510 | 59.2 | 225020 |  |  | 150 | 94.5% | 95% | 93.6% | 95% | 95% | 94.5% | 150 | 95.4% | 95.8% | 94.1% | 95.8% | 95.8% | 95% | Hospitals & Healthcare - HVAC | CWP | Hospitals & Healthcare - HVACCWP | - | - | - | - | - | - | - | - | -
[22 empty] | Utility | Zone | 200 | 94.5% | 95% | 94.5% | 95% | 95% | 95% | 200 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.4% | Hospitals & Healthcare - HVAC | HVACF | Hospitals & Healthcare - HVACHVACF | 7243.2 | 0.261 | 0.276 | 0.261 | 0.26 | 0.758 | 0.907 | 0.758 | 0.694
1 | [21 empty] | Allegheny Power | 2 | [7 empty] | 250 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.8% | Hospitals & Healthcare - HVAC | CTF | Hospitals & Healthcare - HVACCTF | 1032 | 0.222 | 0.245 | 0.222 | 0.217 | 0.675 | 0.869 | 0.675 | 0.594
2 | [21 empty] | Duquesne Light | 2 | [7 empty] | 300 | 95.4% | 95.8% | 95.4% | 95.8% | 96.2% | 95.8% | Education - K-12 | CHWP | Education - K-12CHWP | 1444 | 0.28 | 0.3 | 0.28 | 0.278 | 0.571 | 0.77 | 0.571 | 0.535
3 | [21 empty] | Met-Ed (FirstEnergy) | 1 | [7 empty] | 350 | 95.4% | 95.8% | 95.4% | 95.8% | 96.2% | 95.8% | Education - K-12 | HWP | Education - K-12HWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
4 | [21 empty] | Penn Power (FirstEnergy) | 1 | [7 empty] | 400 | 95.8% | 95.8% | 95.8% | 95.8% | 96.2% | 95.8% | Education - K-12 | CWP | Education - K-12CWP | 1444 | 0.238 | 0.263 | 0.238 | 0.237 | 0.571 | 0.771 | 0.571 | 0.535
5 | [21 empty] | PennElec (FirstEnergy) | 1 | [7 empty] | 450 | 96.2% | 96.2% | 95.8% | 95.8% | 96.2% | 95.8% | Education - K-12 | HVACF | Education - K-12HVACF | 4164.8 | 0.271 | 0.288 | 0.271 | 0.27 | 0.675 | 0.832 | 0.675 | 0.646
6 | [21 empty] | PECO | 1 | [7 empty] | 500 | 96.2% | 96.2% | 95.8% | 95.8% | 96.2% | 95.8% | Education - K-12 | CTF | Education - K-12CTF | 1032 | 0.238 | 0.263 | 0.238 | 0.237 | 0.571 | 0.771 | 0.571 | 0.535
7 | [21 empty] | PPL | 3 | [14 empty] | Education - College & University | CHWP | Education - College & UniversityCHWP | 1718 | 0.283 | 0.304 | 0.283 | 0.28 | 0.599 | 0.796 | 0.599 | 0.548
8 | [37 empty] | Education - College & University | HWP | Education - College & UniversityHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
9 | [37 empty] | Education - College & University | CWP | Education - College & UniversityCWP | 1718 | 0.243 | 0.27 | 0.243 | 0.243 | 0.599 | 0.796 | 0.599 | 0.548
10 | [37 empty] | Education - College & University | HVACF | Education - College & UniversityHVACF | 4580.8 | 0.277 | 0.293 | 0.277 | 0.275 | 0.696 | 0.852 | 0.696 | 0.657
[20 empty] | 0 | 0 | [16 empty] | Education - College & University | CTF | Education - College & UniversityCTF | 1032 | 0.243 | 0.27 | 0.243 | 0.243 | 0.599 | 0.796 | 0.599 | 0.548
Savings Data | [37 empty] | Retail | CHWP | RetailCHWP | 2347 | 0.283 | 0.305 | 0.283 | 0.239 | 0.675 | 0.869 | 0.675 | 0.594
Total Peak kW Reduction |  |  | 0 | [34 empty] | Retail | HWP | RetailHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
Total Annual kWh Savings |  |  | 0 | [34 empty] | Retail | CWP | RetailCWP | 2347 | 0.244 | 0.271 | 0.244 | 0.239 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Retail | HVACF | RetailHVACF | 5537.6 | 0.278 | 0.295 | 0.278 | 0.276 | 0.758 | 0.907 | 0.758 | 0.694
[38 empty] | Retail | CTF | RetailCTF | 1032 | 0.244 | 0.271 | 0.244 | 0.239 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Restaurants - Fast Food | CHWP | Restaurants - Fast FoodCHWP | 2901 | 0.229 | 0.291 | 0.229 | 0.267 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Restaurants - Fast Food | HWP | Restaurants - Fast FoodHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
[38 empty] | Restaurants - Fast Food | CWP | Restaurants - Fast FoodCWP | 2901 | 0.273 | 0.253 | 0.273 | 0.224 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Restaurants - Fast Food | HVACF | Restaurants - Fast FoodHVACF | 6702.4 | 0.266 | 0.282 | 0.266 | 0.264 | 0.758 | 0.907 | 0.758 | 0.694
[38 empty] | Restaurants - Fast Food | CTF | Restaurants - Fast FoodCTF | 1032 | 0.273 | 0.253 | 0.273 | 0.224 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Restaurants - Sit Down | CHWP | Restaurants - Sit DownCHWP | 2160 | 0.284 | 0.307 | 0.284 | 0.279 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Restaurants - Sit Down | HWP | Restaurants - Sit DownHWP | 4959 | 0.278 | 0.321 | 0.278 | 0.275 | 1 | 1 | 1 | 1
[38 empty] | Restaurants - Sit Down | CWP | Restaurants - Sit DownCWP | 2160 | 0.246 | 0.272 | 0.246 | 0.241 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Restaurants - Sit Down | HVACF | Restaurants - Sit DownHVACF | 5246.4 | 0.278 | 0.295 | 0.278 | 0.277 | 0.758 | 0.907 | 0.758 | 0.694
[38 empty] | Restaurants - Sit Down | CTF | Restaurants - Sit DownCTF | 1032 | 0.246 | 0.272 | 0.246 | 0.241 | 0.675 | 0.869 | 0.675 | 0.594
[38 empty] | Office - Large | Other | Office - LargeOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Office - Small | Other | Office - SmallOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Hospitals & Healthcare - Pumps | Other | Hospitals & Healthcare - PumpsOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Hospitals & Healthcare - HVAC | Other | Hospitals & Healthcare - HVACOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Education - K-12 | Other | Education - K-12Other | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Education - College & University | Other | Education - College & UniversityOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Retail | Other | RetailOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Restaurants - Fast Food | Other | Restaurants - Fast FoodOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
[38 empty] | Restaurants - Sit Down | Other | Restaurants - Sit DownOther | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit | Edit
Note on C10: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours, Coincidence Factors, ESF and DSF (as applicable) for motor functions not listed. CHWP: Chilled Water Pump HWP: Heating Hot Water Pump CWP: Condenser Water Pump HVACF: HVAC Fan CTF: Cooling Tower Fan
Note on K10: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on M10: Nominal Efficiency Select Motor Horsepower, Synchronous Speed and Enclosure Type to determine nominal efficiency.
Note on E10: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on J10: Motor Horsepower Select the rated horsepower of the motor.
Note on L10: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on B10: Unique Motor I.D. Provide designation to identify the motor(s).
Note on F10: Motor Configuration Select the appropriate motor configuration. If the motor configuration is not listed, a custom motor protocol must be used. Single: One motor serving the load. Duplex: Two motors serving the load, one as standby.
Note on H10: Manufacturer Provide the motor manufacturer's name.
Note on I10: Model Number Provide the motor model number.
Note on C4: Facility Type Select the appropriate facility type from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours, Coincidence Factors, ESF and DSF (as applicable) for building types not listed.
Note on C5: Utility Select the utility serving the facility from the pull down menu.
Note on N11: VFD on Motor Is there a VFD installed on this motor? Select "Yes" or "No". If existing motor already has a VFD installed, Custom Measure Protocols must be used.
Note on B28: Unique Motor I.D. Provide designation to identify the motor(s).
Note on F28: Motor Configuration Motors can be set up in different configurations; individually, in parallel, in lead-lag. Select the most appropriate configuration for the motor(s).
Note on H28: Manufacturer Provide the motor manufacturer's name.
Note on I28: Model Number Provide the motor model number.
Note on J28: Motor Horsepower Select the rated horsepower of the motor.
Note on K28: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on L28: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on D10: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on D28: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on M28: Nominal Efficiency Select Motor Horsepower, Synchronous Speed and Enclosure Type to determine nominal efficiency.
Note on E28: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on N29: VFD on Motor Is there a VFD installed on this motor? Select "Yes" or "No". If existing motor already has a VFD installed, Custom Measure Protocols must be used.
Note on O11: ESF "Energy Savings Factor" for the VFD. Percentage of energy consumption by motor when VFD is installed.
Note on P11: DSF "Demand Savings Factor" for the VFD. Percentage of peak demand consumption by motor when VFD is installed.
Note on O29: ESF "Energy Savings Factor" for the VFD. Percentage of energy consumption by motor when VFD is installed.
Note on P29: DSF "Demand Savings Factor" for the VFD. Percentage of peak demand consumption by motor when VFD is installed.
Note on C28: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours, Coincidence Factors, ESF and DSF (as applicable) for motor functions not listed. CHWP: Chilled Water Pump HWP: Heating Hot Water Pump CWP: Condenser Water Pump HVACF: HVAC Fan CTF: Cooling Tower Fan

## Glossary
Pennsylvania Act 129 Motor and VFD Audit and Design Tool
GLOSSARY
Cell C2: | "Applicant Name" is the applicant name.
Cell C3: | "Facility Name" is the facility name.
Cell C4: | "Facility Type" is the facility classification. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient.
Cell C5: | "Utility" is the electric distribution company territory where the facility is located.
Cell C6: | "Date Submitted" is the date at which the application was submitted to the program.
Cell K2: | "Project Name" is the name of the project.
Cell K3: | "Survey Completed by (Name)" is the name of the inspector(s) who completed the survey.
Cell K4: | "Spot Measurements Completed by (Name)" is the name of the inspector(s) who completed the spot measurements.
Cell K5: | "Date Survey(s) Completed" is the date at which the surveys were completed.
Column A: | "Line Item" indexes the motors.
Column B: | "Unique Motor I.D.(s)" is an identifier for each motor.
Column C: | "Motor Function" defines the function of the motor or the process served by the motor. There are five pre-defined motor functions: Chilled Water Pump (CHWP), Heating Hot Water Pump (HWP), Condenser Water Pump (CWP), HVAC Supply Fan (HVACF), and Cooling Tower Fan (CTF). All other motor functions must be submitted as a custom measure. The combination of motor function, building type, and utility service territory determines the ESF, DSF, and operating hours (columns O, P and R).
Column D: | "Number of Identical Units" defines the quantity of motors for this particular line item. Motors that are not identical in Manufacturer, Model Number, Motor Function, Motor Configuration, Load Factor, Run Hours, Horsepower, Synchronous Speed, Enclosure Type, or Efficiency must be entered on separate lines.
Column E: | "Load Factor" is the ratio between the actual load and the rated load. Motor efficiency curves typically result in motors being most efficient at approximately 75% of the rated load. The default value is 0.75. Variable loaded motors should use custom measure protocols.
Column F: | "Motor Configuration" is the setup in which the motor operates. For example, a motor may be in a single motor setup, parallel motor setup, a lead-lag setup, or a stand-by setup. Depending on the configuration, the coincidence factor will be changed.
Column G: | "Coincidence Factor" is the percentage of the motor load that is operating during electric system’s summer peak period as defined by Act 129. Heating hot water pumps do not operate during the summer cooling season and therefore the coincidence factor is 0. Chilled water pumps and condenser water pumps operate during the cooling season and therefore have a coincidence factor of 1. Pumps in a duplex or stand-by configuration have a 0.5 coincidence factor to account for the standby condition. Other motor configurations should follow custom protocols to determine the appropriate coincidence factor.
Nameplate Data
Column H: | "Manufacturer" is the maker of the motor.
Column I: | "Model Number" is the specific model number of the motor.
Column J: | "Motor Horsepower" is the rated horsepower of the motor.
Column K: | "Synchronous Speed" is the speed at which an induction motor will operate, which depends on the input power frequency and the number of electrical magnetic poles in the motor. Select either 1200 RPM, 1800 RPM, or 3600 RPM from the drop down menu.
Column L: | "Enclosure Type" is the enclosure of the fan which enables the cooling of motor windings. Select "ODP" for Open Drip Proof enclosure or "TEFC" for Totally Enclosed Fan Cooled from the drop down menu.
Column M: | "Nominal Efficiency" is the ratio of the motor shaft output power to the electric input power. This value is determined by NEMA tables of standard and premium efficiency motors based on motor horsepower, motor speed and motor enclosure type.
VFD
Column N: | "VFD on Motor" is to indicate the presence or absence of a VFD on the motor. If there is a VFD installed, select "Yes". If there is no VFD installed, select "No".
Column O: | "ESF" is the Energy Savings Factor for VFDs or the ratio of the motor energy usage with a VFD installed to the motor energy usage without a VFD installed. Motors with no VFD installed have an ESF of "1.00". This value can be looked up based on the facility type and the motor function.
Column P: | "DSF" is the Demand Savings Factor for VFDs or the ratio of the motor peak demand with a VFD installed to the motor peak demand without a VFD installed. Motors with no VFD installed have a DSF of "1.00". This value can be looked up based on the facility type and the motor function.
Total per Unit
Column Q: | "kW" is the peak demand consumption for one motor in kilowatts.
Column R: | "Operating Hours" is the number of hours that the motor runs in one year. This number is stipulated by building type and motor function.
Column S: | "Annual kWh" is the total annual energy consumption of one motor in kilowatt-hours.
Total all Units
Column T: | "kW" is the peak demand consumption of all the motors.
Column U: | "Annual kWh" is the total annual energy consumption of all the motors.