	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	Public Meeting held December 20, 2007

	Commissioners Present:
	


	      Wendell F. Holland, Chairman                              

	      James H. Cawley, Vice Chairman   

	      Tyrone J. Christy

	      Kim Pizzingrilli


	Letter of Notification of PPL Electric 

Utilities Corporation, filed pursuant to 

52 Pa. Code Chapter 57 Subchapter G,
with respect to the Ebenezer 138/69 kV 

Tap Line in Lower Swatara Township, 

Dauphin County, Pennsylvania.  
	Docket Number:

A-110500F0398



ORDER

BY THE COMMISSION:

On October 12, 2007, PPL Electric Utilities Corporation (PPL Electric) filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(1) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the 
right-of-way.

ii) An HV line which is proposed to be located entirely within a public road.
iii) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.
iv) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.
v) An HV line having a proposed route of 2 miles or less.
Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3), on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Dauphin County Planning Commission, Dauphin County Commissioners, Lower Swatara Township, Lower Swatara Township Planning Commission and Lower Swatara Township Commissioners.  No protests were filed.  No hearings were held.
PPL Electric seeks Commission’s approval to site and construct a       138/69 kV transmission tap line in Lower Swatara Township.  The proposed tap line is required to allow PPL Electric to shift load from the Swatara 69-12 kV Substation which has reached its maximum design capacity level.  Thus, the proposed 138/69 kV tap line, in conjunction with the new Ebenezer Substation, will enable PPL Electric to meet the increasing demand for electricity and improve reliability of service in the Lower Swatara Township area.
PPL Electric states that the proposed Ebenezer 138/69 kV tap line will extend approximately 500 feet from the Hummelstown-Harrisburg #2 138/69 kV Line to the new Ebenezer 69-12 kV Substation, which will be constructed on property owned by PPL Electric near the intersection of Longview Drive and State Road 441 in Lower Swatara Township.  Both the proposed 138/69 kV tap line and the new Ebenezer Substation will be constructed entirely on land already owned by PPL Electric.

The proposed 500 feet long Ebenezer 138/69 kV tap line will be mounted on four steel poles that will each extend approximately 80 feet above the ground.  The proposed tap line will consist of three 556.5 KCMIL 24/7 stand ACSR power conductors.  In addition, there will be a 3/8'' steel overhead ground wire to provide lightning protection for the proposed tap line.  The new 138/69 kV Tap Line will be designed and constructed to operate at 138 kV although, initially, it will operate at 69 kV
PPL Electric anticipates the proposed Ebenezer 138/69 kV Tap Line to cost approximately $325,000.  There will be additional cost costs for the Ebenezer Substation, but no approval is required for the construction of the Ebenezer Substation.  The project has a scheduled construction start date of July 2008, to support the project’s in-service date of May 2009.
PPL Electric states that the project will be designed, constructed, operated, and maintained in a manner that meets or exceeds the National Electrical Safety 
Code (NESC) standards, PPL Electric’s design criteria and safety practices, and all applicable legal requirements.  The proposed project will not create any unreasonable risk of danger to the public health or safety.

PPL Electric states that the proposed project will have no significant additional land use impacts due to the small size of the project.  The entire project will be located on land owned by PPL Electric.  No railroads, communication towers, pipelines, or other utilities will be affected by the proposed project.  The nearest aviation facility is the Harrisburg Airport, which is 2.7 miles from the project location.  The project will have no effect on the airport or flight operations.

PPL Electric states that the project will not impact any unique geological, scenic, or natural areas.  No national natural landmarks, parks, or recreational facilities are located near the project.  The proposed transmission line will not cross any wetlands or other aquatic resources.  PPL Electric will employ its “Specifications for Soil Erosion and Sedimentation Control on Transmission Line Rights-of-Way” as appropriate.
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,


IT IS ORDERED:
That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the Ebenezer 138/69 kV Tap Line in Lower Swatara Township, Dauphin County, Pennsylvania, is hereby approved. 







BY THE COMMISSION,







James J. McNulty








Secretary

(SEAL)
ORDER ADOPTED:  December 20, 2007
ORDER ENTERED:  December 27, 2007
PAGE  
4

