	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	Public Meeting held September 11, 2008

	Commissioners Present:
	

	
	

	James H. Cawley, Chairman
	

	Tyrone J. Christy, Vice Chairman
	

	Robert F. Powelson
	

	Kim Pizzingrilli
	

	Wayne E. Gardner
	

	
	

	Letter of Notification of PPL Electric Utilities Corporation, filed pursuant to 52 Pa. Code Chapter 57 Subchapter G, with respect to the reconstruction of the Lackawanna-Peckville #1 138/69 kV Transmission Line segment in Blakely 

and Archbald Boroughs, Lackawanna County, PA.
	
	Docket Number:

A-2008-2051783 

	
	

	
	


ORDER

BY THE COMMISSION:

On July 15, 2008, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification pursuant to 52 Pa. Code § 57.72(d)(l) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.
(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.
(vi)
An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3), on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Archbald and Blakely Boroughs, Archbald and Blakely Boroughs Planning Commissions, Lackawanna County Planning Commission, Lackawanna County Board of Commissioners, and other interested parties.  No protests were filed.  No hearings were held.


PPL Electric seeks the Commission’s approval for the siting and reconstruction of a 0.5-mile long Lackawanna-Peckville #1138/69 kV transmission line in Blakely Borough and Archbald Borough, Lackawanna County.  This filing is the second of three filings seeking the PUC’s approval of one of three related projects.  


PPL Electric proposes to replace a line segment for a portion of the Lackawanna-Peckville #1 138/69 kV circuit by constructing a new double circuit 138/69 kV steel pole line for approximately 0.5 mile in an easterly direction out of the Lackawanna 230-69 kV Substation parallel to the existing transmission line.  Initially, one circuit will be installed.  From that point, the new line will connect into the existing Lackawanna-Peckville #1 138/69 kV, “H” frame line which continues in a southerly direction to the Peckville 230-69 kV Substation.  The installation of this new line segment will free up the existing Lackawanna-Peckville #1 138/69 kV circuit to establish the rebuilt Lackawanna-East Carbondale 138/69 kV circuit, which was the subject of the first filing before the PUC under Docket No. A-2008-2045409.
PPL Electric states that the new line segment will operate at 69 kV initially; but will be designed and insulated for future 138 kV operation.  The new line will consist of single and multi-pole fabricated weathering steel structures equipped with upswept weathering steel arms, 138 kV polymer insulator assemblies, 3-556.5 KCMIL, 24/7 stranding, ACSR conductors and one 3/8 inch high strength steel overhead ground wire.  All new poles for this segment of the project will be direct embedded, with an approximate height of 90 feet above ground.  All line angle and tap structures will be guyed.  PPL Electric states that the proposed transmission line reconstruction will be done entirely on PPL Electric fee owned property.  No new right-of-way or easements are required for the project.
PPL Electric states that the proposed project is necessary for reliable transmission and distribution of electricity to the public.  Specifically, it is needed to alleviate conductor overloading between the Lackawanna 230-69 kV Substation and Edella 69-12 kV Tap, avoid a sustained interruption of 44 MW of customer load and maintain 69 kV bus voltage along the Lackawanna-East Carbondale 115/69 kV Line.  
PPL Electric states that the project will be designed, constructed, operated and maintained in a manner that meets or exceeds National Electrical Safety Code (“NESC”) standards and all applicable legal requirements.  The proposed project will not create an unreasonable risk of danger to the public health or safety.   
PPL Electric states that the proposed line reconstruction will create minimal land use impacts.  The proposed line segment reconstruction is generally located in woodland and open areas.  The only property to be affected by the proposed reconstruction is owned in fee by PPL Electric.  No railroads, communication towers, pipelines or other utilities will be affected by the proposed project. 
PPL Electric states that the proposed project will not affect any unique geological, scenic or natural areas.  No National Natural Landmarks, parks or recreational facilities are located near the project area.  No regulated waters or wetlands are found within or near the construction area.  PPL Electric will employ its “Specifications for Initial Clearing and Control of Vegetation On or Adjacent to Electric Line Right-of-Way Through Use of Herbicides, Mechanical and Hand Clearing Techniques.”
PPL Electric states that the total estimated cost of the proposed project is approximately $466,000, to be paid for by PPL Electric.  The project is scheduled to start in November 2008 in order to meet an in-service date of November 2009.
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,

IT IS ORDERED:

That the Letter of Notification filed by PPL Electric Utility Corporation regarding the Lackawanna-Peckville #1 138/69 kV transmission line reconstruction in Blakely Borough and Archbald Borough, Lackawanna County, Pennsylvania, is hereby approved.

BY THE COMMISSION,

James J. McNulty

Secretary

(SEAL)

ORDER ADOPTED:  September 11, 2008
ORDER ENTERED:  September 12, 2008
PAGE  
5

