	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	Public Meeting held October 23, 2008

	Commissioners Present:
	

	
	

	James H. Cawley, Chairman
	

	Tyrone J. Christy, Vice Chairman
	

	Robert F. Powelson
	

	Kim Pizzingrilli
	

	Wayne E. Gardner
	

	
	

	Letter of Notification to Duquesne Light Company, filed pursuant to 52 Pa. Code Chapter 57.72 for increasing the voltage of a 2.9-mile long Transmission Line in South Heights Borough and Hopewell Township, Beaver County, PA
	
	Docket Number:

A-2008-2060160

	
	

	
	


ORDER

BY THE COMMISSION:

On August 25, 2008, Duquesne Light Company (“Duquesne Light”) filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(l)(iv), of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the  right-of-way.


(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present                          levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.
(v)
An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi)
An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with

Section 57.72(d) (3) and 57.74(b) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, South Heights Borough,  Hopewell Township, Crescent Township, Hopewell Township Board of Commissioners, Beaver County Board of Commissioners, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.

Duquesne Light seeks Commission’s approval to increase the voltage of a 2.9-mile long transmission line from 69 kV to 138 kV.  The line is located in South Heights Borough and Hopewell Township, Beaver County, Pa.

Duquesne Light proposes to reconfigure existing transmission facilities by combining two existing circuits, one an existing 69kV circuit presently identified as Phillips-Hopewell #1 66145 (“Ckt. 66145”) with an existing 138kV circuit presently identified as Phillips-Crescent Z-23 (“Ckt. Z-23”).  The voltage increase is proposed for the 2.9 mile segment.  Following the proposed voltage upgrade, the resulting circuit will be identified as Crescent-Hopewell Z-25.  To establish the Crescent-Hopewell Z-​25 Ckt., the existing Phillips-Hopewell #1 66145 in the vicinity of Phillips Substation will be connected to the north side conductors of the existing Phillips-Crescent Z-23 138 kV bifurcated conductors, which currently connects Phillips Substation to Crescent Substation.  A new structure will be constructed in the Phillips Substation that will facilitate the connection between the existing Ckts. #66 145 and Z-23.  A second circuit, known as Phillips-Hopewell #2 66146 (“Ckt. 66146”), sharing the same structures as 66145 and presently operating at 69kV will eventually be de-energized. 

Duquesne Light states that the lines consist primarily of lattice steel towers constructed in the 1950’s for operation at 138kV in general compliance with the National Electrical Safety Code (“NESC”) in effect at that time.  Although rated for 138kV, Ckts. 66I45 and 66146 have continued operation at 69kV.  Ckt. Z-23 currently operates at       138kV.
Duquesne Light states that the height of the structures and the span lengths on the upgraded 2.9-mile transmission line will remain the same, as will the structures for the current Ckt. Z-23. The height of the existing structures ranges between 93 feet and 124 feet.  Existing span lengths range from 307 to 1,650 feet, with an average span length for the line at 732 feet.

Duquesne Light further states that the upgraded Ckt. 66145 and Ckt. Z-23 will continue to be three-phase alternating current transmission lines.  Each circuit currently consists of three phase conductors with one shield wire for each circuit.  Each phase conductor for the existing Ckt. 66145 will remain as 795 kcmil 45/7 Aluminum Conductor Steel Reinforced (“ACSR”) conductor and the shield wires will remain as    5/1 6” Stainless Steel conductor.  Each phase conductor for the existing Ckt. Z-23 will remain as 853.7 kcmil 24/13 Aluminum Conductor Aluminum Reinforced (“ACAR”) conductor and the shield wire will remain as 7#8 Alumoweld conductor.

Duquesne Light states that new construction consisting of one steel pole inside Phillips Substation and approximately 630 feet of new conductor from Structure 360-1 within Phillips Substation to Structure 4000 will be required.  This will be completed to facilitate the proposed voltage upgrade of Ckt. 66145 and the relocation of the termination point from Phillips Substation into Crescent Substation for this new 138kV operation.  The new construction will take place entirely on Duquesne Light property.  No other new construction, reconstruction, or modifications, except for routine maintenance items, will be required to increase the voltage from 69kV to 138kV on this new line.
Duquesne Light states that the new line initiates at Crescent Substation and follows the existing Z-​23 circuit for 0.23 miles in a northerly direction.  A new section at Phillips Substation connecting Z-23 with Ckt. 66145 extends 0.12 mile in a northerly direction.  The final segment begins at Phillips Substation and proceeds a distance of approximately 0.5 miles in a general west direction through South Heights Borough and the remainder of the 2.4 miles in a generally north direction through South Heights Borough and Hopewell Township.
Duquesne Light states that the merger of Ckts. Z-23 and 66145 as the new Ckt. Z-25 will support the relocation of distribution facilities from the Phillips Power Station location to an existing, modern, Duquesne Light switching station, namely Crescent Substation.  By bypassing Phillips Substation and supplying Crescent and Hopewell Substations, the new line will help consolidate transmission infrastructure.  This includes the elimination of transmission control equipment from Phillips Power Station and the elimination of redundant equipment originally placed into service to meet the needs of the retired power station.  That unnecessary equipment increases maintenance and chances of failure.




Further, Duquesne Light states that in addition to supporting the new distribution at the expanded Crescent Substation and the consolidation of transmission, the upgrades are part of Duquesne Light’s overall strategy to eliminate 69 kV as a transmission supply voltage.  This strategy was created to address system inefficiencies, age of facilities, and lack of replacement parts.  Increasing the transmission supply from 69kV to 138kV will increase the capacity of the transmission system, decrease the number of transformations to 69kV and consequently reduce losses and investment in 69kV autotransformers, while addressing the need for extensive rehabilitation of aging substations.  As a result, Duquesne Light’s customers will benefit through increased reliability in this area.


Duquesne Light states that the project will be designed, constructed, operated and maintained in a manner that meets or exceeds NESC standards and all standards of the Federal Occupational Safety and Health Administration. 
Duquesne Light states that the proposed increase in voltage of Ckt. 66145 will not substantially alter the right-of-way.  The Line has existed and operated in its present location since the I950s as has Ckt. Z-23.  The size, character, design, or configuration of Ckt. 66145 will not change to increase the voltage of the Line.  The existing right-of-way agreements are written for a “transmission system for the conveyance and distribution of electric current.”  The route of the transmission lines will remain essentially unchanged.  The existing centerline rights-of-way and widths of 30 and 40 feet will also remain unchanged.

Duquesne Light states that the projected cost of this project is $200,000.  The project is scheduled to start in January 2009 and the proposed in-service date for the operation of the upgraded Ckt. 66145 and Ckt. Z-23 at 138 kV is also in January 2009.
The formal Duquesne Light Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,

IT IS ORDERED:



That the Letter of Notification filed by Duquesne Light Company regarding the increase in voltage of a 2.9-mile long transmission line from 69kV to 138kV in South Heights Borough and Hopewell Township, Beaver County, Pennsylvania, is hereby approved.

BY THE COMMISSION,

James J. McNulty

Secretary

(SEAL)

ORDER ADOPTED: October 23, 2008
ORDER ENTERED:  October 23, 2008
PAGE  
6

