	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	

	
	
	

	
	Public Meeting held January 16, 2004

	Commissioners Present:
	


	      Terrance J. Fitzpatrick, Chairman      

	      Robert K. Bloom, Vice Chairman   

	      Glen R. Thomas

	      Kim Pizzingrilli
      Wendell F. Holland


	Letter of Notification of PPL Electric Utilities Corporation filed pursuant to 52 Pa. Code Chapter 57 for modification of the existing Berks-Spring #2 138/69 kV transmission line in Spring Township, Berks County, Pennsylvania


	         Docket Number:               

         A-110500 F0335 



ORDER

BY THE COMMISSION:



On October 23, 2003, PPL Electric Utilities Corporation (“PPL”) filed a Letter of Notification pursuant to 52 Pa. Code §57.72 (d)(1)(vi), of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process when approval is being requested to construct a transmission line where the voltage is proposed to be increased above present levels, where a line is to be reconstructed, or where the line has a proposed length of two miles or less.
   
     
Copies of the siting application were served in accordance with Section 57.72(d)(3) on the Pennsylvania Department of Transportation, Pennsylvania Historical and Museum Commission, Department of Environmental Protection, Berks County Commissioners, Berks County Planning Commission, Spring Township Supervisors and the Spring Township Planning Commission.  A Notice of Transmission Line Construction was published in the newspapers of general circulation in the affected area.  The required fifteen (15) day protest period ended on December 2, 2003.  No protests were filed.  No hearings were held.

   
   
PPL’s Letter of Notification seeks siting approval for modifications to the Berks-Spring #2 138/69 kV Transmission Line in Spring Township, Berks County, Pennsylvania, consisting primarily of the installation of two tap structures necessary to accommodate this project.  Both new structures will be single shaft steel poles installed on concrete foundations.  One structure will be 52 feet in height, the other 65 feet.


Currently, the Berks-Spring #2 Line supplies 102 MVA (Megavolt Amperes) of load to all or parts of seven different substations.  Forecasts indicate that, by the summer of 2004, an outage of the Berks-Spring #1 Transmission Line would cause the load on the Berks-Spring #2 line to exceed its conductor’s emergency rating.  To address this problem, PPL proposes to construct a new 69 kV transmission line (the Berks-Lavino 69 kV Transmission Line), approximately 1100 feet in length.  The new line will be constructed for double circuit operation, although only one circuit will be installed initially.  The new 69 kV line will connect to the Berks-Spring #2 138/69 kV Line in two locations through the installation of two new tap structures.  The proposed Berks-Lavino 69 kV Line will reduce the loading on the Berks-Spring #2 138/69 kV Line by assuming the supply to all or parts of four substations currently supplied by the Berks-Spring #2 Line.  The new arrangement will redistribute and better balance the load on the 69 kV system in the affected area such that supply could be maintained to all of the substations supplied by the Berks-Spring #1 and #2 138/69 kV transmission Lines in the event of an outage of either one of those lines.


PPL states that all line construction and modifications are being done on existing PPL fee-owned property or existing PPL right-of-way.  No additional right-of-way is required.  PPL states that no railroads, communications towers, pipelines or other utilities will be affected by the proposed reconstruction.  Additionally, PPL states that a project review by the Pennsylvania Historical Museum and Commission has determined that this project will have no effect on archeological resources and that the project will not affect any unique geological, scenic or natural areas. 


The project will be designed, constructed, operated and maintained in accordance with National Electrical Safety Code requirements, PPL’s design criteria and safety practices, and all applicable legal requirements.


PPL states that modification of the Berks-Spring #2 138/69 kV Transmission Line is scheduled to begin in February 2004 and be completed in May 2004.



The formal PPL Letter of Notification and the manner in which it was filed conforms with the requirements of 52 Pa. Code §57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with applicable law or Commission policy regarding transmission line siting; THEREFORE,

IT IS ORDERED:
     

That the Letter of Notification filed by PPL with respect to the modification of the existing Berks-Spring #2 138/69 kV transmission line in Spring Township, Berks County, Pennsylvania is hereby approved.






BY THE COMMISSION







James J. McNulty







Secretary
(SEAL)

ORDER ADOPTED:  January 16, 2004
ORDER ENTERED:  January 20, 2004



PAGE  
4

