	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	Public Meeting held October 27, 2005

	
	

	Commissioners Present:
	

	
	

	Wendell F. Holland, Chairman

	James H. Cawley, Vice Chairman

	Bill Shane

	Kim Pizzingrilli

	Terrance J. Fitzpatrick



	Letter of Notification of PPL Electric Utilities Corporation filed pursuant to 52 Pa. Code Chapter 57 with respect to the Dorneyville 138/69 kV Tap Rearrangement in Upper Macungie Township, Lehigh County, Pennsylvania
	Docket Number:

A-110500 F0362

	
	

	
	


ORDER

BY THE COMMISSION:

On August 4, 2005, PPL Electric Utilities Corporation (“PPL”) filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(1)(vi), of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process when approval is being requested to construct a transmission line where the voltage is proposed to be increased above present levels, where a line is to be reconstructed, or where the line has a proposed length of two miles or less.
PPL’s Letter of Notification proposes to rearrange a section of the existing Dorneyville 138/69 kV Tap in Upper Macungie Township, Lehigh County, Pennsylvania in order to support the conversion of the Dorneyville Substation from 69-12 kV to 139-12 kV operation.  PPL states the conversion is necessary to alleviate overloading two of the 69 kV transformers at PPL’s Wescosville 500-230-138-69 kV Substation, which currently feed the Dorneyville Substation.
Copies of the siting application were served in accordance with Section 57.72(d)(3) on the Pennsylvania Department of Transportation, Pennsylvania Historical and Museum Commission, Department of Environmental Protection, Lehigh County, Lehigh Valley Planning Commission, Upper Macungie Township Board of Supervisors, Upper Macungie Township and the Upper Macungie Township Planning Commission.


A Notice of Transmission Line Construction was published in the newspapers of general circulation in the affected area.  The required fifteen (15) day protest period ended on September 9, 2005.  No protests were filed.  No hearings were held.
The Dorneyville 69-12 kV Substation is presently supplied from the #1 and #2 69 kV transformers at the Wescosville 500-230-138-69 kV Substation via the double circuit Hosensack-Wescosville 69 kV Lines and the double circuit Dorneyville 138/69 kV Tap.  PPL submits that there are two problems at the Wescosville Substation.  First, during hot summer days, load on the #1 69 kV transformer has occasionally exceeded the normal transformer rating of 200 Mega Volt-Amperes (“MVA”) which, in turn, caused the 69 kV transmission system to be operated outside of its normal configuration.  Secondly, the unanticipated loss of either the #1 or the #2 transformer would interrupt service to about 65 MW of load, or approximately 10,000 customers, until repairs could be made.
To resolve the problems discussed above, PPL proposes to transfer the Dorneyville Substation load from the 69 kV transmission system to the 138 kV transmission system.  The load transfer will be completed by removing one span of double circuit 69 kV transmission line, in order to isolate the Dorneyville 138/69 kV Tap from the Hosensack-Wescosville #1 and #2 69 kV Lines.  Then, approximately 500 feet of new double circuit 138 kV transmission line will be constructed to connect the Dorneyville Tap to the Siegfried-Wescosville #1 and #2 138 kV Transmission Lines.  In order to accept load at 138 kV, the existing transformers at the Dorneyville Substation will be replaced with 138-12 kV units.  The proposed solution will reduce the forecasted load on the Wescosville transformers by 38 MVA and, thereby, eliminate potential transformer overloading problems at the Wescosville Substation.

The proposed line arrangement will require the construction of approximately 500 feet of transmission line and the removal of approximately 250 feet of line.  Three new poles will need to be installed to construct the new section of line.
PPL states that all of the proposed construction will take place on property that PPL already owns.  No additional land or right-of-way is required.  
PPL states that no railroads, airports, communications towers, pipelines or other utilities will be affected by the proposed modifications.  Additionally, PPL states that a project review by the Pennsylvania Historical and Museum Commission has determined that this project will have no effect on archeological resources and that the project will not affect any unique geological, scenic or natural areas.
PPL states that the project will be designed, constructed, operated and maintained in accordance with National Electrical Safety Code requirements, PPL’s design criteria and safety practices, and all applicable legal requirements.
PPL states that construction of this project is scheduled to begin as soon as possible after the Commission grants siting approval in order to support the project’s 
in-service date of May 2006.
The formal PPL Letter of Notification and the manner in which it was filed conforms with the requirements of 52 Pa. Code §57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with applicable law or Commission policy regarding transmission line siting; THEREFORE,
IT IS ORDERED:
That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the Dorneyville 138/69 kV Tap Rearrangement in Upper Macungie Township, Lehigh County, Pennsylvania is hereby approved.







BY THE COMMISSION







James J. McNulty







Secretary

(SEAL)
ORDER ADOPTED:  October 27, 2005
ORDER ENTERED:  November 1, 2005



PAGE  
4

