	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	
	

	
	Public Meeting held June 22, 2006

	
	

	Commissioners Present:
	

	
	

	Wendell F. Holland, Chairman

	James H. Cawley, Vice Chairman

	Bill Shane

	Kim Pizzingrilli

	Terrance J. Fitzpatrick

	

	

	

	Letter of Notification of Duquesne Light Company filed pursuant to 52 Pa. Code Chapter 57 to increase the voltage of a 5.2 mile long transmission line in West Mifflin Borough, City of Duquesne, North Versailles Township, Wilmerding Borough, and Monroeville Borough, Allegheny County, Pennsylvania.
	Docket Number:

A-110150 F0034

	
	

	
	


ORDER

BY THE COMMISSION:

On March 31, 2006, Duquesne Light Company (“Duquesne”) filed a Letter of Notification pursuant to 52 Pa. Code §57.72 (d)(1)(vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process when approval is being requested to construct a transmission line where the voltage is proposed to be increased above present levels, where a line is to be reconstructed, or where the line has a proposed length of two miles or less.

The Letter of Notification proposes to increase the voltage of an existing 5.2 mile transmission line (“the Line”) from 69 kilovolts (kV) to 138 kV.  The Line is  one circuit of a double-circuit transmission line identified as the Dravosburg-Wilmerding line (“Dravosburg-Wilmerding “).  The second circuit on Dravosburg-Wilmerding presently operates at the 138 kV level.  Dravosburg-Wilmerding connects the Duquesne Dravosburg Substation to the Duquesne Wilmerding Substation.
The existing 69 kV Dravosburg-Wilmerding line was upgraded for operation at 138 kV in 1958 and 1966.  The upgrade consisted of replacing the steel crossarms with bowed laminated wood crossarms, modifying each tower with a single steel peak to accommodate one common shield wire for both circuits, tower and foundation reinforcement, replacing and relocating towers, and replacing the conductors and insulators.  Duquesne states that the height of the structures and the span lengths will remain the same.
The Line will continue to be three-phase alternating current transmission line.  Each circuit of Dravosburg-Wilmerding (including the Line) consists of three phase conductors with one shield wire common to both circuits.  Each phase conductor is 24/13 Aluminum Conductor Alloy Reinforced (“ACAR”) conductor.  The shield wire is a 7#8 Alumoweld conductor.  No new construction, reconstruction, or modifications, except for routine maintenance items, will be required to increase the voltage from 69 kV to 138 kV on the Line.
Duquesne states that concerns have arisen regarding the limited transmission resources supplying the northeastern areas of Duquesne’s service territory.  Increasing the transmission supply from 69 kV to 138 kV will increase the capacity of the transmission system, decrease the number of transformations to 69 kV and consequently reduce losses and investment in 69 kV autotransformers, while addressing the need for extensive rehabilitation of aging substations.  

Duquesne avers that increasing the voltage of the Line will support the proposed distribution rehabilitation at Wilmerding Substation.  The upgrades planned to Wilmerding Substation are part of Duquesne’s overall strategy to establish the eastern area source and eliminate 69 kV as a transmission supply voltage because:
(1) Duquesne’s aging 69 kV substation equipment requires increased maintenance on obsolete equipment with limited parts availability.

(2) Conversion from 69 kV to 138 kV will reduce transmission system losses by eliminating double transformations resulting form the use of numerous 138 – 69 kV autotransformers to serve islands of 69 kV and by reducing current flow on the transmission line conductors due to the increased voltage level.

(3) There is a need to improve voltage on the existing 69 kV system, which typically experiences the lowest system voltage following certain transmission system contingencies.

In 1966, the Line was modified and upgraded to increase the voltage from 69 kV to 138 kV.  Although the Line has continued to operate at 69 kV since that time, the modifications were designed and constructed, and the Line has been operated and maintained, to meet or exceed the requirements of the National Electrical Safety Code (“NESC”).  The operation and maintenance procedures for these Lines conform to Duquesne’s procedures for line clearance and vegetation management on rights-of-way.  These standards meet or exceed all relevant NESC standards and all standards of the Federal Occupational Safety and Health Administrations.
Duquesne states that in accordance with the provisions of 52 Pa. Code §57.72 (d)(3), a copy of this Letter of Notification was served by certified mail upon those who would have otherwise been entitled to receive a copy of an application or notice of filing an application as set forth in §57.74 (52 Pa. Code §57.74).  No protests were filed.  No hearings were held.  
The formal Duquesne Letter of Notification and the manner in which it was filed conforms with the requirements of 52 Pa. Code §57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with applicable law or Commission policy regarding transmission line siting; THEREFORE,

IT IS ORDERED:

That the Letter of Notification of Duquesne Light Company filed pursuant to 52 Pa. Code Chapter 57 to increase the voltage of an existing 5.2 mile long transmission line in West Mifflin Borough, City of Duquesne, North Versailles Township, Wilmerding Borough, and Monroeville Borough, Allegheny County, Pennsylvania, is hereby approved.







BY THE COMMISSION







James J. McNulty







Secretary

(SEAL)

ORDER ADOPTED:  June 22, 2006
ORDER ENTERED:  June 26, 2006



PAGE  
5

