	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	
	

	
	Public Meeting held November 30, 2006

	
	

	Commissioners Present:
	

	
	

	Wendell F. Holland, Chairman

	James H. Cawley, Vice Chairman

	Kim Pizzingrilli

	Terrance J. Fitzpatrick

	

	

	Letter of Notification of Duquesne Light Company filed pursuant to 52 Pa. Code Chapter 57 to increase the voltage on a 1.2-mile segment of an existing   transmission line from 69 kV to 138 kV.  The transmission line is located in Indiana Township, Allegheny County, Pennsylvania.
	Docket Number: A-110150 F0036

	
	

	
	


ORDER

BY THE COMMISSION:

On September 22, 2006, Duquesne Light Company (“Duquesne Light”) filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(1) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character design, or configuration of the proposed HV line does not substantially alter the   right-of-way.

ii) An HV line which is proposed to be located entirely within a public road.

iii) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

iv) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way. 

v) An HV line having a proposed route of 2 miles or less.


Copies of the siting application were served in accordance with Section 57.72(d)(3) on the Pennsylvania Department of Transportation, Pennsylvania Historical and Museum Commission, Department of Environmental Protection, Indiana Township Board of Supervisors, Allegheny County Council, and other interested parties.  No protests were filed.  No hearings were held.



Duquesne Light’s Letter of Notification seeks approval to increase the voltage on a 1.2-mile segment of an existing double circuit transmission line (“the Line”) from 69 kV to 138 kV.  The existing two-circuit transmission line known as Colfax-Pine Creek Line (“Colfax-Pine Creek”) connects the Duquesne Light Colfax Substation to the Duquesne Light Pine Creek Substation.  The Line begins at Pine Creek Substation and proceeds a distance of 1.2 miles in a generally easterly direction.  The entire 1.2 mile of the Line is located within Indiana Township, partially, on existing 30-foot rights-of-way, existing centerline rights-of-way, and on Duquesne Light’s property.  



Duquesne Light states that the Line is needed to support a new distribution substation, California Substation, as part of its plan to address the need for extensive rehabilitation of aging substations and increase reliability of its entire transmission system. 



Duquesne Light states that no new construction, reconstruction, or modifications, except for routine maintenance items, will be required to increase the voltage from 69kV to 138kV on the Line.  This is because the Line was modified and upgraded for operation at 138kV in 1966 but has continued to operate at 69kV since that time.  



Duquesne Light states that the height of the structures and the span lengths on the Line will remain the same.  The height of the existing structures ranges from 94 to 114 feet above the ground.  The existing span lengths range from 65 to 1149 feet, with typical span lengths varying between 400 and 750 feet.  The maximum span length on the Line is 1149 feet.  The Line will continue to be a three-phase alternating current transmission line.  Each circuit of Colfax Pine Creek (including the Line) consists of three phase conductors with one shield wire common to both circuits.  Each phase conductor on the Line is 853.7 kcmil 24/13 Aluminum Conductor Alloy 
Reinforced (“ACAR”) conductor and shield wire is a 7#8 Alumoweld conductor.


According to Duquesne Light, the 1966 modifications were designed and constructed, and the Line has been operated and maintained, to conform to Duquesne Light’s transmission and distribution construction standards and Duquesne Light’s procedures for line clearance and vegetation management on rights-of-way.  These standards meet or exceed all relevant National Electrical Safety Code standards and all standards of the Federal Occupational Safety and Health Administration.


Duquesne Light states the project has an in-service date of December 2006. 



The formal Duquesne Light’s Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,


IT IS ORDERED:



That the Letter of Notification filed by Duquesne Light to increase the voltage on a 1.2-mile segment of an existing transmission line from 69 kV to 138 kV in Indiana Township, Allegheny County, Pennsylvania, is hereby approved. 








BY THE COMMISSION,







James J. McNulty








Secretary
(SEAL)

ORDER ADOPTED:  November 30, 2006
ORDER ENTERED:  December 5, 2006



PAGE  
4

