BEFORE THE
PENNSYLVANIA PUBLIC UTILITY COMMISSION
Kathleen Sylvester




:

C-20055453

William J. Finkler




:

C-20055473

James Pugh





:

C-20065849



Formal Complainants


:

And






:

PA PUC Law Bureau,




:

And 






:

Office of Consumer Advocate



:



Intervenors



:







:


v.





:








:

Washington Park Water Company


:

Kathleen Sylvester




:

C-20055455

William J. Finkler




:

C-20055473

James Pugh





:

C-20065850



Formal Complainants


:
And






:

PA PUC Law Bureau,




:

And






:

Office of Consumer Advocate



:

Intervenors



:






:


v.





:








:

Washington Park Sanitary Company


:

Initial Decision
Before

Ember S. Jandebeur
Administrative Law Judge

TABLE OF CONTENTS
1I.
HISTORY OF THE PROCEEDINGS


5II.
STIPULATED FINDINGS OF FACT


12III.
FINDINGS OF FACT


37IV.
DISCUSSION


37A.
Issues


38B.
Principles of Law


381.
Burden of Proof


392.
Statutory Obligations


40C.
Complaints Against WP Water


411.
Low Water Pressure and Outages


452.
Inadequate Supply and Storage


473.
Metering


494.
Small Diameter Delivery Pipes


505.
Commission Precedent


52D.
Complaints Against WP Sanitary


531.
Blockages in Collection Mains


542.
Commission Precedent


553.
Severe Malodors


59E.
Civil Penalty


591.
Civil Penalty Assessed Against WP Water


622.
Civil Penalty Assessed Against WP Sanitary


633.
Civil Penalty Assessed Against Carl Kresge


674.
Civil Penalty Assessed Against Sandra Kresge


68V.
CONCLUSIONS OF LAW


71VI.
ORDER





I.
HISTORY OF THE PROCEEDINGS TC "I.
HISTORY OF THE PROCEEDINGS" \f C \l "1" 
This Initial Decision grants in part and denies in part the relief requested by the three Formal Complainants, PUC Law Bureau, and Office of Consumer Advocate against Washington Park Water Company, Inc. and Washington Park Sanitary Company, Inc.  A civil penalty is assessed against Washington Park Water Company, Inc., Washington Park Sanitary Company, Inc., and against Carl Kresge, president and Sandy Kresge, owner.
Formal complaints were filed by numerous individuals against Washington Park Water, Inc. and Washington Park Sanitary, Inc. (“WP Water” and “WP Sanitary” or “Company” or “Companies”).  Two state agencies intervened by statutory right.  The current owners, Carl and Sandra Kresge, acquired WP Water and WP Sanitary in 1985
 and have operated the Companies since that time.  (Respondent Exhibit E)  Carl Kresge is president of the Companies; his wife, Sandra Kresge, is the purported and listed owner.  The WP Water system currently serves approximately 150 single-family and apartment customers in a portion of Washington Township, Wyoming County, which is known as Washington Park.  The Company holds a Pennsylvania Department of Environmental Protection (DEP) permit for water supply but does not have a valid NPDES (National Pollutant Discharge Elimination System) permit to discharge waste.  Both Companies currently hold Public Utility Commission (PUC or Commission) certificates of public convenience.
On October 19, 2005, the following individuals filed complaints:  Brian P. DeGroot against WP Water at Docket No. C-20055451, Cory Pries
 against WP Water at Docket No. C-20055452, Kandi Jo Madill against WP Water at Docket No. C-20055454 and against WP Sanitary at Docket No. C-20055456, and Kathleen Sylvester against WP Water at Docket No. C‑20055453 and WP Sanitary at Docket No. C-20055455.  On October 20, 2005, Joseph Yakoski filed a complaint against WP Water at Docket No. C-20055460.  On October 21, 2005, Leigh Powell filed a complaint against WP Water at Docket No. C-20055468.  On October 24, 2005, William J. Finkler filed a complaint against WP Water at Docket No. C-20055473, and Lisa Higgins filed a complaint against WP Water at Docket No. C-20055472.  On November 10, 2005, Fred T. Reibeling filed a complaint against WP Water at Docket No. C-20055556 and against WP Sanitary at Docket No. C-20055557.  On January 9, 2006, James Pugh filed a complaint against WP Water at Docket No. C-20065849 and against WP Sanitary at C‑20065850.
Complainants Sylvester, Finkler and Pugh filed single formal complaints
 against WP Water and WP Sanitary that mirrored one another; i.e., the complaints combined the allegations against the two Companies into one formal complaint.  Each complaint was docketed under two separate numbers to reflect the fact that the Companies have separate certificates of public convenience.  (See Transcript February 27, 2006, at 124-126.) 

The Companies filed Answers to the formal complaints.

On November 30, 2005, the PUC Law Bureau (Law Bureau) filed a Notice of Intervention.

On December 20, 2005, a Telephonic Prehearing Conference call was held with numerous Complainants, the Respondent, Law Bureau, and the Office of the Consumer Advocate (OCA) participating.

On January 4, 2006, OCA filed a Notice of Intervention.
On January 4, 2006, a Hearing Notice was mailed to all of the Parties
 setting forth, among other things, the date, time, and location for the February 27, 2006 hearing regarding their Complaints. 

On February 27, 2006, a hearing in the matter was held.  Complainants Kathleen Sylvester and William Finkler appeared, as did the Respondent and Intervenors.
On March 10, 2006, the undersigned administrative law judge (ALJ), issued an Initial Decision dismissing the complaints of formal complainants who did not appear at the February 27, 2006 hearing pursuant to 52 Pa. Code § 5.345.  That decision was made final without further action by the Commission on May 11, 2006.
Further hearings took place on May 23, 2006, and June 18 and 19, 2006.  Complainant Pugh and witnesses for the Companies, the Law Bureau and the OCA testified.  At my request, the OCA and the Law Bureau filed joint proposed findings of fact on August 9, 2006.  Revised joint proposed findings were filed on August 29, 2006.  

Main Briefs were filed on September 15, 2006, by OCA, and on September 20, 2006, by the Law Bureau.  A Reply Brief was filed on October 4, 2006, by the Companies.  Reply/Surrebuttal Briefs were filed by OCA and the Law Bureau on October 20, 2006.
The record in this matter was reopened by Interim Orders dated February 14 and April 4, 2007.  The February Interim Order required additional documents to be submitted by the Companies.  The April 4, 2007, Interim Order allowed a brief extension of time at the Companies’ request.  The record closed by that same Interim Order on April 6, 2007.  The matter is ready for disposition.
On June 6, 2007, the Office of Consumer Advocate (“OCA”) filed a Petition for a Commission Order Instituting a Proceeding to Order the Acquisition of W.P. Water Company, Inc. and W. P. Sanitary Company, Inc. (“W.P.”) pursuant to 66 Pa. C.S. § 529. (“Petition”)

Concurrently with the mandatory takeover Petition, OCA filed a separate petition for ex parte emergency relief under Commission regulations at 52 Pa. Code § 3.2.  The petition for emergency order was docketed at P‑00072312.  Vice Chairman Cawley granted that petition, in part, by Emergency Order dated June 15, 2007.  The Emergency Order was ratified at the Public Meeting of June 21, 2007.

On June 22, 2007, OCA filed a Motion to Consolidate the Application of W.P. Sanitary Co., Inc. for Approval of Abandonment of Service at Docket No. A‑230550F2000 (the Application) and the Petition for a Commission Order Instituting a Proceeding to Order the Acquisition of W.P. Water Co. Pursuant to 66 Pa. C.S. § 529 at Docket No. P-00072313 (the Petition).
At the July 11, 2007 Public Meeting, the Commission ordered that an investigation be instituted into whether the Commission should order a capable public utility to acquire WP Water and WP Sanitary pursuant to 66 Pa. C.S. § 529.  The same order consolidated the investigation at Docket No. I-00070114, and the Application proceeding at Docket No. A-230550F2000.  The matter is currently in voluntary mediation.
II.
STIPULATED FINDINGS OF FACT TC "II.
STIPULATED FINDINGS OF FACT" \f C \l "1" 
The following findings of fact have been stipulated to by the Companies, OCA and the Law Bureau.
1. Currently, bills do not include the following:
a. beginning and ending dates of the billing period;
b. a statement directing the ratepayer to “register any question or complaint about the bill prior to the due date” with the address and telephone number where the ratepayer may initiate the inquiry or complaint with the Companies; 
c. a statement that a rate schedule, an explanation of how to verify the accuracy of a bill and an explanation of the various charges is available for inspection in the local business office of the Companies; 
d. a customer account number, rather than an invoice number.  (OCA Statement No. 2 at 2-3, Appendix II.)
2. The Companies agree to modify bills to comply with 52 Pa. Code § 56.15 and 52 Pa. Code § 69.251.  (Statement No. K-11 at 3-4; Tr. July 19, 2006, (Kresge) at 108.) 

3. The Companies agree to provide status reports to the Commission and the OCA on a monthly basis for the first six months following entry of a Commission Order in this case and on a quarterly basis thereafter, which include a representative sample of actual customer bills for the previous month (with customer names and account numbers deleted) to ensure that the necessary modifications are made to the bill format pursuant to 52 Pa. Code § 65.3.  (Tr. July 19, 2006, (Kresge) at 99; OCA Statement No. 2 at 6; Statement No. K-11 at 3-4.)  

4. The number given to customers calls the Kresge family’s home, which is approximately 46 miles or one hour driving time from the Washington Park system.  (Tr. May 23, 2006, (Kresge) at 123, 125.)
5. On October 15 and 16, 2005, the answering machine did not properly record customer calls.  (Statement No. K-8 at 4.)
6. The Companies agree to maintain customer complaint records in compliance with 52 Pa. Code § 56.15 and 52 Pa. Code § 69.251.  (Tr. July 19, 2006, (Kresge) at 97-98.) 

7. The Companies agree to provide status reports to the Commission and the OCA on a monthly basis for the first six months following entry of a Commission Order in this case and on a quarterly basis thereafter, which include a list of all customer complaints and the Company’s resolution of each for the previous month/quarter.  (Tr. July 19, 2006, (Kresge) at 99; OCA Statement No. 2 at 6.)
8. The Company has elected to provide written notice of the start and end of all boil water advisories via an electronic sign installed on Washington Park Road viewable to drivers entering Washington Park.  (Tr. July 19, 2006, (Kresge) at 90.)  

9. The Companies agree to provide status reports to the Commission and the OCA on a monthly basis for the first six months following entry of a Commission Order in this case and on a quarterly basis thereafter, which include a copy of all boil water advisories (both declaring and lifting the advisory).  (Tr. July 19, 2006, (Kresge) at 99; OCA Statement No. 2 at 6.)
10. Well No. 3, not shown on the system map (Schedule TLF-2), is located on Debbie Drive.  (Tr. July 19, 2006, (Kresge) at 187, July 18, 2006, (Fought) at 145.)
11. There are currently approximately 150 customers served by the WP Water system.  (OCA Statement No. 1 at 4; Tr., July 18, 2006, (Fought) at 133.)
12. The topography of the Washington Park service area is not level.  In general, the higher elevations in the development are to the west and to the north.  (Tr. February 27, 2006, (Sylvester) at 65; OCA Statement No. 1 at 4.)
13. Between October 5 and October 15, 2006, well no. 2 was offline for replacement of a motor and pump.  (Statement No. K-8 at 3.)
14. On October 15, 2006, well no. 3 shut down due to mechanical failure.  (Statement No. K-8 at 3.)
15. Well no. 2 was put back online on October 15, 2006, and it took approximately one day for water pressure to build back up on that line.  (Statement No. K-8 at 4.)
16. At least twenty new homes have been added to the system since 1993.  (Tr. February 27, 2006, (Sylvester) at 45, 61; Schedule TLF-4 at 5.)  

17. New homes are currently being added on Debbie Drive.  (Tr., February 27, 2006, (Finkler) at 128.) 

18. When the water levels in the wells are very low, sediment and air may enter the distribution system.  (Statement K-9 at 3.)
19. The Company agrees that additional finished water storage should be constructed to improve pressure on the system.  (Schedule TLF-3; OCA Statement No. 1 at 8; Tr. July 19, 2006, (Kresge) at 176-178, 188.)  

20. Customers’ water usage is not metered and customers are charged flat rates for service.  (Statement No. K-10 at 2-3; OCA Statement No. 1 at 4; Tr., July 19, 2006, (Kresge) at 103.)
21. In its Order in Docket No. M-82038
, entered April 26, 1991, the Commission directed WP Water to provide metered service to its existing 52 customers by March 1995 and further directed the Company to meter all new customers as their services are connected.  (Tr. July 19, 2006, (Lash) at 29-30; Exhibit PS-6.)
22. The Company agrees that meters should be installed for all customers.  (Schedule TLF-3 at 2; Tr. July 19, 2006, (Kresge) at 187.)
23. A rough cost estimate for constructing a new water well source and finished water storage tank and installing customer water meters in 2006 is $700,000.  (OCA Statement No. 1 at 9; Schedules TLF-4, TLF-5.)
24. On July 15, 2006, WP Water’s electric utility experienced a power outage and as a result, WP Water customers were without electricity and water.  (Tr. February 27, 2006, (Lash) at 24, 26, 55.)
25. The Washington Park system has no back up generation equipment in service.  (Tr. July 19, 2006(Kresge) at 142, 186.)
26. The Company agrees that a back-up generator should be installed.  (Tr., July 19, 2006, (Kresge) at 186.)
27. The collection sewer mains installed in several streets, including Thomas Drive, are made of vitreous clay with tar joints.  (Tr. May 23, 2006, (Kresge) at 84, 104.)
28. The wastewater system is subject to excessively high flows from infiltration/inflow.  (OCA Statement No. 1 at 11, Schedule TLF-10; Statement No. K-10 at 3.)
29. WP Sanitary Company (WP Sanitary) has not obtained bids or cost estimates for an infiltration/inflow study.  (Tr. July 18, 2006, (Fought) at 158-159; Statement No. K-10 at 2.)
30. Tree roots grow into the joints in the vitreous clay pipe and can block the flow of wastewater.  (Tr. May 23, 2006, (Kresge) at 82, 92, 109, 113; (Pugh) at 33-34.)  This has been an ongoing problem.  (Tr. May 23, 2006, (Kresge) at 96, 100-101, 102, 113.) 

31. Waste sludge has not been hauled from the treatment plant since at least 2001.  (OCA Statement No. 1 at 13; Tr. July 18, 2006, (Kresge) at 46.)
32. If sludge is not hauled away, it is discharged to the receiving stream.  (OCA Statement No. 1 at 13; Tr. July 18, 2006, (Kresge) at 54-58 and (Holmes) at 96, 99.)
33. When the flow into the treatment plant greatly exceeds its capacity, sludge is washed through to the receiving stream.  (Tr. July 18, 2006, (Kresge) at 54-58, May 23, 2006, (Holmes) at 181, July 18, 2006, (Holmes) at 96, 99.)
34. Each day, the plant experiences a peak flow rate that is greater than it can effectively treat.  (Tr. July 19, 2006, (Kresge) at 180.)
35. Excessive infiltration/inflow deposits solids in the treatment tanks, which displaces volume and reduces capacity for treatment.  (Tr. July 18, 2006, (Fought) at 161, May 23, 2006, (Holmes) at 182-183.) 

36. A measurement of flow coming into the wastewater treatment plant is required to obtain information for an infiltration/inflow study.  (Tr. July 19, 2006, (Fought) at 211-213, 218-220, May 23, 2006, (Holmes) at 181.)
37. Estimating flow into the wastewater treatment plant based on measurements from wells is insufficient due partly to significant infiltration/inflow on the system.  (Tr. July 19, 2006, (Fought) at 211-213, 219.)
38. An improperly operated wastewater treatment plant can result in the plant becoming septic.  (OCA Statement No. 1 at 13.)
39. Inadequate or improper operation and maintenance accelerate deterioration and necessary replacement of plant.  (Tr. July 18, 2006, (Fought) at 160.)
40. Septic plants have a strong hydrogen sulfide smell, similar to rotten eggs.  (OCA Statement No. 1 at 13.  Tr. July 18, 2006, (Fought) at 146, and May 23, 2006, (Holmes) at 217.)
41. The Company agrees that the sources of excessive infiltration/inflow must be studied and corrected.  (OCA Statement No. 1 at 17, Schedule TLF-10 at 3.)
42. The Company agrees that an equalization tank should be installed, with necessary DEP approvals.  (OCA Statement No. 1 at 17, Schedule TLF-10 at 3.)  The size of the equalization tank should be determined as part of an infiltration/inflow study.  (Tr. July 18, 2006, (Fought) at 197.)
43. The Company agrees that tertiary treatment should be installed or the plant size should be increased, with necessary DEP approvals.  (OCA Statement No. 1 at 17, Schedule TLF-10 at 3; Tr. July 18, 2006, (Kresge) at 31.)
44. The Company agrees that the splitter box (diverter) should be replaced.  (OCA Statement No. 1 at 17, Schedule TLF-10 at 3; Tr. July 19, 2006, (Kresge) at 169.)
45. The Company agrees to adjust diffusers to improve roll in the treatment plants.  (Tr. July 19, 2006, (Kresge) at 170.)  

46. The Company agrees that, during dry weather, the treatment plant tanks should be emptied, cleaned of sediment, repainted and repaired as necessary.  (OCA Statement No. 1 at 18.)  

47. The Company agrees that a working flow meter should be installed, which measures both treatment plant trains.  (OCA Statement No. 1 at 18, Schedule TLF-10 at 3; Tr., July 19, 2006, (Kresge) at 174-175; Statement No. K-9 at 5.)
48. The Companies cannot afford to make necessary improvements to its systems without outside financing.  (Statement No. K-9 at 2-3; Schedule TLF-3 at 1; Holmes Exhibit 2; Tr., July 18, 2006, (Kresge) at 19, 28, 43, 59, 61, 76, and July 19, 2006, (Kraus) at 118-119.)
49. WP Water operated at a loss in 2004, 2003, 2002 and 2001 and at a gain of $1,226 in 2005.  (Exhibit PS-4; Annual Report of WP Water Company, Inc. for the years ended December 31, 2005, 2004, 2003 and 2002; Tr. July 19, 2006, (Kraus) at 118.)
50. WP Sanitary operated at a loss in 2005, 2004 and 2003 and at a gain of $959 and $1,771 in 2002 and 2001, respectively.  (Exhibit PS-7; Annual Report of WP Sanitary Company, Inc. for the years ended December 31, 2005, 2004, 2003 and 2002, at 35; Tr. July 19, 2006, (Kraus) at 118.)  

III.
FINDINGS OF FACT TC "III.
FINDINGS OF FACT" \f C \l "1" 
51. WP Water and WP Sanitary are regulated utilities that provide water and wastewater services, respectively, to residents of the Washington Park subdivision in Tunkhannock, Pennsylvania.

52. The current owners, Carl and Sandra Kresge, purchased WP Water and WP Sanitary from a Mr. Thomas; they have owned and operated the systems since that time.  Statement No. K-9 at 2; Tr. May 23, 2006, (Kresge) at 78.
53. Carl Kresge is president of the Companies; his wife, Sandra Kresge, is the listed owner.  2005 PUC Annual Report of WP Water at 3, 11; 2006 PUC Annual Report of WP Sanitary at 3, 9.

54. WP Water and WP Sanitary are managed out of the Kresges’ residence, as is Mr. Kresge’s well drilling company and the remains of another Kresge endeavor, the now bankrupt Wilbar Realty, Inc. 
55. All WP customers are currently billed $38.25 per month for water and sewage service.  It is a flat rate billing; the customers are not metered.

56. Installation of meters and metered rates may encourage WP Water customers to conserve water and thereby help address customers’ water pressure problems.

57. It is possible to implement metered rates through a revenue-neutral rate filing.  Tr. July 19, 2006, (Kraus) at 115-116.

58. Carl and Sandra Kresge are the primary customer contacts for emergency calls.  In their absence, calls are picked up by a family member or a voice message machine.  OCA Statement No. 2-S at 2, Appendix III-S; Tr. February 27, 2006, (Sylvester) at 59.  

59. Mr. Kresge indicated he kept copies of written complaints in a file, but did not keep oral complaints.  Tr. May 23, 2006, (Kresge) at 120. 

60. WP Water and WP Sanitary do not maintain written service complaints showing the name and address of the complainant, the date and character of the complaint and the final disposition of the complaint.  Tr. May 23, 2006, (Kresge) at 118-120.

WP Water
61. WP Water applied for a PENNVEST loan in 1994 to develop a new water well source, construct a finished water storage tank and install customer water meters.  OCA Statement 1 at 8, 9; Schedule TLF-4; Statement No. K-9 at 2, 3; Tr. July 18, 2006, (Kresge) at 73-75.

62. Mr. Kresge was preliminarily notified that his application for PENNVEST loans for WP Water was approved around November 29, 1994.  Tr. July 18, 2006, (Kresge) at 73.

63. Mr. Kresge believed his PENNVEST application (WP Water only) was “hampered” or sabotaged by a DEP employee.  Tr. July 18, 2006, (Kresge) at 70‑71.

64. The loan for WP Water was never finalized; WP Water did not receive PENNVEST funds.  Tr. July 18, 2006, (Kresge) at 71-75.
65. On February 21, 1997, PENNVEST notified Mr. Kresge, via certified mail, that due to issues regarding Wilbar Realty, Inc., numerous obligations would have to be met by the Kresges and WP Water before the loan could be consummated.  The obligations were not met.  Fought at TLF‑5, Tr. July 18, 2006, (Kresge) at 75-76.
66. Wilbar Realty, Inc., a company owned by the Kresges, and referred to in the PENNVEST letter cited in the Findings of Fact 66, filed for bankruptcy protection.  Tr. July 18, 2006, (Kresge) at 52.
67. How Wilbar Realty, Inc. is faring since the bankruptcy filing was not made part of the record in this proceeding.
68. Complainants Sylvester and Finkler live on opposite sides of Jeanne Drive.

69. Complainant Sylvester has never received any notice prior to a water outage.  Tr. February 27, 2006, (Sylvester) at 45.
70. Complainant Sylvester estimated that she lost all water twice per year for periods lasting from one day to three or four days.  Tr. February 27, 2006, (Sylvester) at 58.  
71. Complainant Sylvester experienced water outages approximately twice per year in the past few years, which last from one day to three or four days.  Tr. February 27, 2006, (Sylvester) at 58.  

72. Complainant Sylvester never received notice of a boil water advisory by mail or television.  She received only one notice by mail regarding the lifting of a boil water advisory, dated October 31, 2005.  Tr. February 27, 2006, (Sylvester) at 45-46; Exhibit KS-2. 
73. Complainant Finkler did not receive notice of the one to two day outage in summer 2005.  Tr. February 27, 2006, (Finkler) at 101.  

74. Complainant Finkler did not receive notice of the October 2005 water outage.  Tr. February 27, 2006, (Finkler) at 103.  Complainant Finkler did receive notice by television that the boil water advisory was lifted, followed by a mailed notice confirming the same.  Tr. February 27, 2006, (Finkler) at 103-104.  
75. Complainant Finkler experienced outages in summer 2005 and October 2005.  Tr. February 27, 2006, (Finkler) at 101-102.
76. WP Water experienced lengthy outages in summer 2005, October 2005 and July 2006.  Tr. February 27, 2006, (Sylvester) at 36-37, 73, and (Finkler) at 101-02, 111 and July 19, 2006, (Lash) at 24, 26, 55.
77. During outages, customers must buy water to meet their household needs.  Tr. February 27, 2006, (Sylvester) at 37, 85.  

78. The WP Water distribution system consists of approximately 23% 2-inch diameter pipe, 24% 3-inch diameter pipe, 15% 4-inch diameter pipe and 38% 6-inch diameter pipe.  Tr. July 18, 2006, (Fought) at 142; Schedule TLF-2.

79. Pipe diameter is inversely related to pressure loss due to friction, such that pressure loss is greater in smaller diameter pipe.  OCA Statement No. 1 at 8; Tr. July 18, 2006, (Fought) at 174-175.

80. Depending on the flow rate, the friction loss in a 3-inch diameter pipe is approximately 25 to 30 times greater than the friction loss in a 6-inch diameter pipe for the same flow rate.  OCA Statement No. 1 at 8.
81. Customers residing on streets with larger diameter mains may still receive water that flowed through smaller diameter pipe.  Tr. July 18, 2006, (Fought) at 143-144.
82. Water pressure varies inversely with pipe elevation, such that customers who reside at lower elevations on the system have greater water pressure than customers who reside at higher elevations.  OCA Statement No. 1 at 4.  

83. Complainants Sylvester and Finkler reside at higher elevations in Washington Park.  Tr. February 27, 2006, (Sylvester) at 30 and (Finkler) at 100; Statement No. K-8 at 4.  

84. WP Water customers, particularly those residing at higher elevations, experience periodic low pressure and water outages.  Statement No. K-12; Tr. February 27, 2006, (Sylvester) at 30, 32, 36-39; (Finkler) at 100-102, 106, and July 19, 2006, (Kresge) at 179.  

85. Complainants Sylvester and Finkler have experienced severe, recurrent occurrences of low pressure and water outages in the last two to three years.  Tr. February 27, 2006, (Sylvester) at 30, 32, 36-39; (Finkler) at 100-102, 106.  

86. Due to low water pressure, WP Water customers are frequently unable to take showers, do laundry, wash dishes or flush toilets.  Tr. February 27, 2006, (Sylvester) at 33, 54, 58, 63, (Finkler, Sylvester) at 105-06.  

87. Complainant Sylvester’s water pressure is lower before and after work, on weekends and in the spring and summer.  Tr. February 27, 2006, at 32.
88. Complainant Finkler’s water pressure is constantly low.  Tr. February 27, 2006, at 113.
89. Complainant Sylvester testified that during the summer of 2005, water pressure was the worst she has experienced.  Tr. February 27, 2006 at 32.  

90. The average daily water demand on the system is approximately 29,000 gallons or 20.14 gallons per minute.  OCA Statement No. 1 at 4, Schedule TLF-1, Tables 1w, 3w.  

91. The WP Water system’s maximum day demand is estimated to be 36.25 gallons per minute.  WP Water’s three wells produce a safe yield of 31 gallons per minute.  Accordingly, the system’s total source capacity is 5.25 gallons per minute less than the estimated maximum day demand.  OCA Statement No. 1 at 5, Schedule TLF-1, Table 2w, 3w.

92. With the largest producing well out of service, the system’s safe yield is 19 gallons per minute or 1.14 gallons per minute less than its average daily water demand.  OCA Statement No. 1 at 4, Schedule TLF-1, Tables 2w, 3w.

93. WP Water does not have sufficient water sources to consistently satisfy its customers’ needs.  OCA Statement No. 1 at 5; Tr. July 18, 2006, (Kresge) at 74-75, and July 19, 2006, (Kresge) at 176.
94. The severity of low-pressure problems has increased over the years.  Tr. February 27, 2006, (Sylvester) at 58, 61.  

95. Complainant Finkler’s low water pressure is a daily problem.  Tr. February 27, 2006, at 106, 111.
96. No party provided test results for water psi.  Complainants Finkler and Sylvester have been completely without water numerous times, sometimes for days, establishing that on those occasions, WP Water was not providing water at 25 psi.  Mr. Kresge does not dispute this.  Tr. July 19, 2006 at 179.
97. The WP Water system should have at least 7,380 gallons to 15,660 gallons of finished water storage.  WP Water has only one 3,000 gallon tank.  OCA St. 1 at 6.  

98. A 3,000 gallon hydro-pneumatic tank actually contains less than 3,000 gallons of water because air takes up part of the volume.  OCA St. 1 at 6.  

99. Additional finished water storage would help address pressure issues caused by the insufficient well capacity.  OCA Statement No. 1 at 8, Schedule TLF-3; Tr. July 18, 2006, (Fought) at 143.
100. For six months or more, WP Water had a strong chlorine smell and a mossy smell.  Tr. February 27, 2006 (Sylvester) at 40-42, (Finkler) at 106, 117-18; May 23, 2006, (Pugh) at 48.  

101. Following the October 2005 outage, water was cloudy.  (Tr. February 27, 2006, (Finkler) at 118.)  At times there is “stuff floating in” the water.  Tr. February 27, 2006, (Sylvester) at 40.  

102. At times, sediment is left in the sink after the water drains out.  Tr., February 27, 2006, (Finkler) at 105, 118.  

103. Both Complainants Sylvester and Finkler filter their water.  Tr. February 27, 2006, (Sylvester) at 76-77, (Finkler) at 111.  

104. Complainant Finkler provides bottled water for his daughter to drink and brush her teeth.  Tr. February 27, 2006, at 111.
WP Sanitary

105. Complainant Pugh lives on Thomas Drive in the Washington Park subdivision.  Tr. May 23, 2007, (Pugh) at 32. 
106. In December 2005, Mrs. Pugh called the Kresges, spoke to Mr. Kresge’s daughter, and told her that she (Mrs. Pugh) had an emergency because wastewater levels were rising in the manhole.  Mrs. Pugh did not receive any response to her call.  Tr. May 23, 2006, (Mrs. Pugh) at 71.
107. Mr. Kresge had allowed Mr. and Mrs. Pugh to call Roto-Rooter on their own behalf as well as on the behalf of their (Pugh’s) neighbors prior to 2000.  The Kresges and Pughs had a falling out over a tree in the Pughs’ yard; after that, the Pughs no longer called Roto-Rooter directly.  Tr. May 23, 2007, (Mrs. Pugh) at 74.
108. A tree on the Pugh’s property is within 50 feet of the centerline of the Washington Township Road named Thomas Drive.  Tr. May 23, 2006, (Kresge) at 88, 93.

109. Tree roots in the WP Sanitary mains can cause wastewater to back up into customers’ service laterals.  Tr. May 23, 2006, (Kresge) at 81, 113.

110. Complainant Pugh and Mr. Kresge have had numerous conversations and disagreements concerning a tree in Complainant Pugh’s yard and whether the tree’s roots interfere with WP Sanitary’s underground lines.  Tr. May 23, 2006, (Pugh) at 9, 59, 103-104.

111. Complainant Pugh maintains his tree is not within any right-of-way.  (Tr. May 23, 2007, at 20.)  Complainant Pugh thinks that his tree’s roots are “more than likely” within a right-of-way.  Complainant Pugh’s testimony regarding this tree is contradictory.  Tr. May 23, 2007, at 57.

112. Mr. Kresge told Complainant Pugh that the October 2005 flooding was caused by Complainant Pugh’s tree roots.  Tr. May 23, 2007, (Pugh) at 39.

113. Mr. Kresge spoke to Washington Township about tree roots infiltrating the WP Sanitary system.  Tr. May 23, 2006, at 86.

114. Mr. Kresge asked Washington Township to remove trees within its (the Township’s) right-of-way.  Tr. May 23, 2006, at 112.

115. Mr. Kresge believes the Pugh tree and other trees on Thomas Drive are within the Washington Township right-of-way.  According to Mr. Kresge, the Township denies the trees are in the Township’s right-of-way.  Tr. May 23, 2006, at 86.

116. Mr. Kresge has recommended to Mr. Pugh that the Pughs have the controversial tree removed.  Tr. May 23, 2006, at 98.

117. In 2001, when Mr. Kresge examined and performed work on his sanitary lines crossing Thomas Drive, he found roots that he believed were from Mr. Pugh’s tree in the sanitary lines.  Tr. May 23, 2006, at 104.

118. Most people have roots in their lateral lines.  Tr. May 23, 2006, at 105.

119. Mr. Kresge understands and agrees that he must pay to have tree roots removed from the WP Sanitary lines.  Tr. May 23, 2006, at 111.
120. Approximately every other year WP Sanitary must clear roots from its lines.  Tr. May 23, 2006, at 113.

121. No Party followed through to determine ownership of the trees that are believed to have caused WP Sanitary infiltration problems.

122. Tar joints are conducive to infiltration and inflow.  (Tr. May 23, 2006, (Kresge) at 84, and July 18, 2006,(Kresge) at 36-37.)  For this reason, clay pipe with tar joints are no longer commonly installed in collection systems.  Instead, “O-ring” joints, with a tighter seal, have been commonly used for sanitary sewers since the late 1950’s.  Tr. July 18, 2006, (Fought) at 165-166, 195, 207, (Holmes) at 98-99.
123. WP Sanitary has the authority to direct customers to disconnect any sump pumps and footer drains from the system, which if present, would contribute to inflow.  OCA St. 1 at 11; WP Sanitary Tariff, 2nd revised p.5; Tr. July 19, 2006, (Fought) at 144-45.  

124. Complainant Pugh has a manhole cover near his yard.  He stated that two days before, and one day before, the May 23, 2006 hearing, there was sewage sludge around the outside of the manhole cover.  He did not provide any other dates of this occurring, nor did he provide any pictures or corroborating statements from other witnesses.  Tr. May 23, 2006 at 23.

125. Complainant Pugh has seen sewage and toilet paper on the outside of the manhole cover since the Kresges have owned WP Sanitary.  Tr. May 23, 2006, at 44, 65.

126. Complainant Pugh takes the cover off the manhole in his yard and looks inside it.  Tr. May 23, 2007, at 24, 44-45, 62.

127. The Pughs check the level of sewage in the manhole because when it rises, they telephone the Kresges to tell them (the Kresges) that there might be a blockage.  Tr. May 23, 2006, at 63-64.

128. After the Pughs called the Kresges to report high levels in the manhole, they (the Pughs) would see Roto-Rooter out working on the lines.  Tr. May 23, 2006, at 69.
129. Excessive infiltration and inflow can contribute to wastewater backing up into customers’ service laterals.  OCA Statement No.1 at 15.
130. Control of infiltration and inflow is part of the normal operation of any wastewater system.  Tr. July 18, 2006, at 166-68.
131. WP Sanitary has “manholes that need to be repaired.”  Tr. May 23, 2006, (Kresge) at 82.
132. Customers located upstream of blockages in the WP Sanitary mains are subject to flooding if check-valves are not installed and working properly.  Tr. May 23, 2006, (Kresge) at 117, and July 19, 2006, (Fought) at 220-221.  

133. Rising wastewater levels in the manhole near Complainant Pugh’s home indicated that there was a blockage in the WP Sanitary lines that caused the wastewater to back up.  Tr. May 23, 2006, (Kresge) at 100, 102.
134. On October 13, 2005, Complainant Pugh’s basement was flooded with wastewater.  Tr. May 23, 2006, (Pugh) at 26-28. 
135. Complainant Pugh’s basement flood amounted to 2-3” of wastewater.  Tr. May 23, 2006, (Pugh) at 41.

136. Complainant Pugh’s basement is 3 or 4 times larger than the Commission’s Scranton hearing room, which is about 16x33’.  Tr. May 23, 2006, at 42. 

137. Complainant Pugh’s wife telephoned WP Sanitary after the October 13, 2005, wastewater flood in their basement.  On October 14, 2005, Mr. Kresge went to the Pughs’ home.  Tr. May 23, 2006, (Pugh) at 39, 58.

138. Roto-Rooter responded to the October 13, 2005 wastewater flood in the Pughs’ basement.  Tr. May 23, 2006, (Pugh) at 59.

139. After the October 13, 2005 flood, Mr. Kresge had Roto-Rooter cut tree roots from one end of Thomas Drive to the other.  Three manholes were accessed and cleared of tree roots.  Tr. May 23, 2006, (Kresge) at 99.

140. Complainant Pugh indicated that the quantity of sewage in his basement was more than the quantity of waste produced by his home alone.  Tr. May 23, 2006, (Pugh) at 16, 41-42; Exh. P-3 A-D.
141. Complainant Pugh has a check valve on the service lateral entering his home.  The check valve is part of what Mr. Pugh calls a grinder pump and was installed two days after his basement flooded in October 2005.  Tr. May 23, 2006, (Pugh) at 51-52, 61, (Kresge) at 94.  
142. There was no rainfall in the days prior to Complainant Pugh’s basement being flooded.  Tr. May 23, 2006, (Pugh) at 28.
143. Complainant  Pugh and his family checked levels in the manhole near his property on a frequent basis.  When levels rise, they move everything out of their basement because they fear that sewage will back up into their home.  Tr. May 23, 2006, at 44-46, 51.
144. In 2005, Mrs. Pugh called Mr. Kresge numerous times to warn him that the sewage levels in the manhole were rising.  Tr. May 23, 2006, at 71.
145. Each time Mr. or Mrs. Pugh called, Mr. Kresge or his wife called Roto-Rooter and had blockages in the collection mains cleared.  Tr. May 23, 2006, (Kresge) at 80-81, 96, 104, 111,117, (Pugh) at 64, 66, 69, (Pugh) at 70-71, 73.
146. No party subpoenaed or otherwise provided Roto-Rooter as a witness to appear and provide evidence on the number of times or the reasons why Roto-Rooter serviced the Washington Park subdivision.

147. Complainant Pugh’s testimony was difficult to follow.  He indicated that due to his medication he becomes confused.  Tr. May 23, 2006, at 6, 13, 33-35, 77.

148. Only Complainant Pugh’s testimony that appeared cogent and reliable is used in this Initial Decision.  (See also FoF 154.)
149. When the mixed liquor in the WP Sanitary aeration tanks do not have a proper roll, it indicates improper aeration.  OCA Statement No. 1 at 12.
150. James Holmes, a witness for OCA, has a Bachelor of Science degree in Agriculture and a Master of Science degree in Microbiology.  Mr. Holmes has worked for the Department of Environmental Protection (DEP) in the Water Quality Bureau (WQB) since 1980 and, specifically, in the WQB’s Operations Section since 1985.  As a field inspector and a supervisor, he has monitored WP Sanitary (not WP Water) since 1986.  Tr. May 23, 2006, (Holmes) at 127-28.

151. Mr. Holmes was subpoenaed at the request of the OCA and testified on behalf of OCA.

152. From May 23, 2005 to May 23, 2006, Mr. Holmes inspected WP Sanitary over 15 times.  That level of frequency is not typical.  Tr. May 23, 2006, at 129.

153. Mr. Holmes inspected WP Sanitary from outside its fence.  Tr. May 23, 2006, at 129.

154. From outside the WP Sanitary fence, Mr. Holmes can perform the following inspection tasks:  observe the aeration tanks and clarifiers and take a sample of the discharged effluent.  Tr. May 23, 2006, at 130.

155. During Mr. Holmes’ September 8, 2005 inspection of WP Sanitary, he noticed a “very severe” sewage/septic odor.  Tr. May 23, 2006, at 133.

156. During Mr. Holmes’ September 13, 2005 inspection of WP Sanitary, he noticed a “severe strong septic odor.”  Tr. May 23, 2006, at 134.

157. The malodor was detected at the plant itself and at the receiving stream.  Tr. May 23, 2006, at 139, 175.

158. Mr. Kresge blamed the September 2005 malodors on the season; i.e., it “is a constant summer problem.  The stream goes dry, the stream begins to get an odor.”  “This has been a terrible, long, on-running thing.”  Tr. July 18, 2006, (Kresge) at 27.

159. The malodor Mr. Holmes detected at WP Sanitary’s treatment plant was worse than the odors he has detected at other treatment plants.  Mr. Holmes did not conduct any air pollution analyses.  Tr. May 23, 2006, (Holmes) at 190-191.

160. Even a properly run wastewater treatment plant has odors, but the odors would not be categorized as a “terrible, long, on-running thing” nor as “severe malodors.”  Tr. July 18, 2006, (Kresge) at 27, (Fought) at TLF-7 Holmes investigation 08/22/2005.

161. No treatment was being provided at the treatment plant on September 8, 2005, and September 13, 2005.  Tr. May 23, 2006, (Holmes) at 175.
162. Mr. Holmes’ September 8, 2005 inspection resulted in a DEP Compliance Order being issued to Carl Kresge.  Tr. May 23, 2006, (Holmes) at 135, Holmes Exh. 1.
163. On September 8, 2005, the splitter box was directing flow to one treatment train, providing unequal distribution.  Overload on one side or the other can cause malfunction.  Tr. May 23, 2006, (Holmes) at 184-185.

164. The Kresges provided a written response to the DEP Compliance Order, consisting of denials, a “limited funds” excuse, and a request for help.  Holmes Exh. 2.

165. On October 19, 2005, Mr. Holmes provided a written response to the Kresges’ letter informing the Kresges that proper operation of WP Sanitary within its [NPDES] permit was clearly the responsibility of the Kresges.  Holmes Exh. 3.

166. At the time of the hearing in 2006, WP Sanitary had not complied with the DEP Compliance Order issued September 8, 2005.  Tr. May 23, 2006, (Holmes) at 137-138.

167. Mr. Holmes concluded that the WP Sanitary plant was in disrepair, provided no treatment to its effluent, and described the stream to which the plant discharged as “atrocious” and stated he had never seen “a stream worse in 27 years.”  Tr. May 23, 2006, at 137.

168. Mr. Holmes, having worked for DEP since 1980, and as a supervisor since 1996, and as a water quality specialist, understands proper sewage treatment plant operations well.
169. Based upon Mr. Holmes’ sworn testimony and exhibits, WP Sanitary is neither operated nor maintained properly.
170. On April 18, 2006, 34 days prior to the May 23, 2006 hearing, DEP employees (Holmes and L. Narocki) conducted an inspection of WP Sanitary and took a series of photographs.  Those photographs comprise Holmes Exhs. 4-1 through 4-21.  Tr. May 23, 2006, (Holmes) at 139, 152.
171. A splitter box receives all raw sewage from the community connected to it.  Tr. July 18, 2006, at 7.
172. Holmes Exh. 4-1 shows a splitter box with an accumulation of solids and paper.
173. When Mr. Kresge bought WP Sanitary, there was only one splitter box; he added another in 1992 as the customer base increased.  Tr. July 18, 2006, at 7.

174. Mr. Kresge admits there are overflows of WP Sanitary’s splitter box.  Tr. July 18, 2006, at 10.
175. Holmes Exh. 4-2 showed the splitter box with paper debris outside the box indicating at one point the splitter box had overflowed or that a WP Sanitary employee put the debris there and did not clean it up.  Tr. July 18, 2006, at 10, 13-14.
176. Mr. Kresge did not want flow going to “one train.”  When the splitter box screens are clean, the flow runs evenly to both trains.  Tr. July 18, 2006, at 15.

177. It is not disputed that flow from the community to the sewage plant should flow equally between WP Sanitary’s two treatment trains.  Tr. July 18, 2006, (Kresge) at 15, and May 23, 2006, (Holmes) at 175, 185.

178. WP Sanitary has problems with toweling being clogged in the splitter boxes.  Tr. July 18, 2006, (Kresge) at 16.

179. Toweling came apart in pieces, went over the weir, through the clarifier, and into the receiving stream.  Tr. July 18, 2006, (Kresge) at 34.

180. The WP Sanitary employee, “Mike,” was scheduled to clean the splitter boxes daily.  No proof was offered that Mike consistently met the cleaning schedule.  Tr. July 18, 2006, (Kresge) at 17.

181. Solids flowing through to the contact tank can occur twice daily.  Tr. July 18, 2006, (Kresge) at 27.

182. When high usage occurred daily, the solid material passed through WP Sanitary’s process directly into the receiving stream.  Tr. July 18, 2006, (Kresge) at 28.

183. Overflow occurred when the pipes took in more water than they could handle, such as occurred during a rain, or something would block the pipes.  Tr. July 18, 2006, (Kresge) at 45.

184. Mr. Kresge blames DEP for not helping him remodel his plant.  Tr. July 18, 2006, at 29.

185. DEP does not provide engineering consulting or remodeling for private parties.  Tr. July 18, 2006, (Holmes) at 93.

186. According to Mr. Kresge, WP Sanitary needs tertiary treatment in the form of a sand filter.  Tr. July 18, 2006, (Kresge) at 30.

187. Mr. Kresge did not investigate the cost of tertiary treatment.  Tr. July 18, 2006, (Kresge) at 30.

188. Mr. Holmes’ opinion is that tertiary treatment is “more treatment than actually is needed at this plant.”  If WP Sanitary was operated properly, it would meet permit limits without tertiary treatment.  Tr. July 18, 2006, (Holmes) at 91.

189. Mr. Kresge testified that a device that would “move and let water flow through and the refuse go through, let the toweling would (sic) come up and drop off into a container that you would haul away” would alleviate the problems with the clogging splitter boxes.  Tr. July 18, 2006, at 19.

190. WP Sanitary had and continues to use equipment that cannot effectively handle the waste coming into WP Sanitary’s two treatment trains.
191. Holmes Exh. 4-3 shows a chlorinator.
192. Holmes Exh. 4-4 shows contact tanks.

193. WP Sanitary’s chlorine contact tank gets “loaded” with green slime because of toweling going past the splitter boxes or the comminuter.  Tr. July 18, 2006, at 10, 20.

194. Mr. Kresge replaced the comminuter with screens because the comminuter ground up towels and allowed the towel fragments to pass into the treatment process.  Tr. July 18, 2006, at 10, 22.

195. The “fluffy” material [toweling or toweling fragments] will not settle out.  Tr. July 18, 2006 at 20.

196. A quantity of “fluffy” material ended up in the chlorine tanks that should never have passed into the chlorine tanks.  Tr. July 18, 2006 at 20, 22.

197. There are solids in WP Sanitary’s chlorine contact tank.  Tr. July 18, 2006 at 25.

198. Mr. Kresge blamed the solids in the WP Sanitary system on toweling that he alleged the WP Sanitary customers are flushing.  It is not toilet paper.  Tr. July 18, 2006, at 25.

199. WP Sanitary is overloaded on a daily basis.  Tr. July 18, 2006 at 26.

200. Mr. Kresge blames the WP Sanitary overload on DEP.  Tr. July 18, 2006, at 26.

201. DEP is neither the owner nor operator of WP Sanitary, and therefore, not responsible for the mismanagement of WP Sanitary.

202. More homes are being built in Washington Township and the new homes hook into WP Sanitary.  WP Sanitary “can’t handle it.”  Tr. July 18, 2006, at 26.

203. Holmes Exh. 4-5 showed WP Sanitary’s discharge pipe at the receiving stream.  Mr. Holmes testified that the sunshine area in the picture shows the deposition of solids.

204. Holmes Exh. 4-6 shows clear water.
205. Holmes Exh. 4-7 shows a reflection of WP Sanitary’s fence, and the discharge pipe at the top of the picture.  Mr. Holmes testified that the picture showed cloudy water to the left indicating a buildup of solids in the stream.  Tr. May 23, 2006, at 145.

206. Holmes Exh. 4-8 showed a brownish buildup of solids in the receiving stream.  “Very disgusting” was Mr. Holmes’ testimony concerning the buildup.  Holmes Exh. 4‑8 shows a line of solids, i.e., human feces, or sewage sludge on the rocks.  Tr. May 23, 2006, (Holmes) at 145-146.

207. Holmes Exh. 4-9 is a depiction of the receiving stream downstream from WP Sanitary’s discharge pipe.  The picture showed the solids being mixed into the receiving stream.  Tr. May 23, 2006, at 145.

208. Both Holmes Exh. 4-8 and 4-9 are photographs downstream from the WP Sanitary discharge pipe.  Tr. May 23, 2006, at 145.
209. Holmes Exh. 4-10 shows human feces or solids in the receiving stream.  Tr. May 23, 2006, at 146-147.
210. Holmes Exh. 4-11 shows solids in the receiving stream.  The photograph also shows a stringy product known as Sphaerotilus that grows in sewage sludge.  Mr. Holmes called Sphaerotilus a fungus, which is incorrect; Sphaerotilus is a bacteria.  The tubular appearance of Sphaerotilus is a distinctive characteristic.  Tr. May 23, 2006, at 147, 148.

211. Holmes Exh. 4-12 shows the WP Sanitary discharge pipe.  At the left corner of the photograph are solids collecting in the receiving stream.  Tr. May 23, 2006, at 148.

212. Holmes Exh. 4-13 shows the discharge pipe at the top of the picture, and solids in the receiving stream.  Tr. May 23, 2006, at 148.

213. Holmes Exh. 4-14 is a close picture of WP Sanitary wastewater going into the contact tank.  According to Mr. Holmes, the flow visible in this picture should be “basically clear.”  The WP Sanitary wastewater is not clear.  Tr. May 23, 2006, at 149.

214. Holmes Exh. 4-15 showed two pipes with unequal flow.  The pipe in the top left of the photograph has noticeably more discharge than the pipe on the right of the photograph, evidencing unequal loading.  Transcript (May 23, 2006) Holmes at 149‑150.

215. Holmes Exh. 4-16 evidenced unequal aeration in the tank in the fore of the photograph.  Unequal aeration causes improper aeration of the wastewater.  Tr. May 23, 2006, at 150.
216. Holmes Exh. 4-17 shows the WP Sanitary splitter box and clear evidence of overflow and spillage of paper products.
217. Holmes Exh. 4-18 is the same splitter box as in Exh. 4-17, but showed a different side and additional overflow of debris and paper products.
218. Holmes Exh. 4.17 and 4.19 show improper operation of WP Sanitary.

219. Holmes Exh. 4-19 is a photograph downstream of the plant.  The stream is a mixed shade of gray across the width of the stream.  Tr. May 23, 2006, at 151.

220. Holmes Exh. 4-20 was taken ¼ mile downstream of WP Sanitary.  It showed a deposition of solids, that the stream was grey at least 1000 feet downstream of the treatment plant and that the stream continued to be affected. Tr. May 23, 2006, at 151.

221. Holmes Exh. 4-21 was taken on the other side of the road from where Exh. 4-20 was taken and showed water flowing from the pipe creating a hole.  The water in the hole is a murky grey from sewage.  Tr. May 23, 2006, at 152.

222. Mr. Holmes instructed Len Narocki of his (Holmes’) staff to conduct a site visit at WP Sanitary on May 4, 2006, 19 days before the hearing in this matter.  That site visit resulted in a series of photographs marked as Holmes Exhs. 5-1 through 5-19.  Tr. May 23, 2006, at 152-154.

223. Holmes Exh. 5-1 is a picture of the receiving stream, above the WP Sanitary discharge pipe, with an object in it.  The stream above WP Sanitary’s discharge is clear.  Mr. Holmes did not know who placed the object, or why it was there.  Tr. May 23, 2006, at 154‑155.

224. Holmes Exh. 5-6 is significant in that at the top right of the photograph, before reaching the WP Sanitary discharge pipe, the stream is clear; at the discharge pipe the stream becomes murky, and at the lower left corner of the photograph one can see sewage solids building up on the rocks in the stream.  Tr. May 23, 2006, at 157.

225. Holmes Exh. 5-7 through 5-10 each evidence collection of sewage solids in the receiving stream downstream of WP Sanitary’s discharge.  Exh. 5-10 shows a significant quantity of sludge collecting on the floor of the receiving stream.  Tr. May 23, 2006, at 158.
226. Holmes Exh. 5-11 is a shot taken looking upstream at clear water and in the fore of the photograph, one sees a pipe. WP Sanitary’s actual discharge pipe is behind the pictured pipe and therefore not visible; below the pictured pipe, one can see the stream is cloudy.  Tr. May 23, 2006, at 158.

227. Holmes Exh. 5-15 through 5-19 are direct photographs of built up sewage solids in the receiving stream.  Tr. May 23, 2006, at 159-160.

228. An NPDES permitted receiving stream should not show any build up of solids.  Tr. May 23, 2006, at 210.
229. The Holmes and Narocki photographs (Holmes Exhs. 4-1 through 4-21 and Holmes Exhs. 5-1 through 5-19) show that the WP Sanitary customers are not getting the service for which they pay a monthly service fee.  Tr. May 23, 2006, at 172.
230. The water “expelled” from WP Sanitary’s treatment plant goes into “somebody’s water supply.”  Tr. May 23, 2006, at 185-186.

231. The unequally distributed load to the splitter box shows that the WP Sanitary customers do not get adequate service.  Tr. May 23, 2006, at 185.

232. The WP Sanitary treatment plant is not operated properly.  Tr. May 23, 2006, (Holmes) at 174.

233. WP Sanitary’s discharge is not properly treated.  Tr. May 23, 2006, (Holmes) at 210.

234. The stream to which WP Sanitary discharges is a perennial stream that gets low in the summer but still flows; it is not stagnant.  Tr. May 23, 2006, at 193, 198, Tr. July 18, 2006, at 84.

235. It is not disputed that rocks can contribute to the collection of solids.  Tr. May 23, 2006, at 199.
236. Mr. Kresge says he can fix the WP Sanitary plant if someone else provides the money.  Tr. July 18, 2006, (Kresge) at 43.

237. A properly run wastewater treatment plant produces sludge that must be hauled away and disposed of properly.

238. Mr. Kresge testified that WP Sanitary is “finally getting some sludge.”  Tr. July 18, 2006, at 46.

239. The last time WP Sanitary hauled sludge away was in 2001.  Tr. July 18, 2006, at 46.

240. WP Sanitary gets “gully washers” that wash WP Sanitary’s collected sludge out to the receiving stream.  Mr. Kresge estimated “99 percent of my sludge is somewhere down in Harrisburg.”  Tr. July 18, 2006, (Kresge) at 54, 57-58.

241. Sludge builds up daily; if WP Sanitary is not “wasting sludge” (i.e., having it hauled away and disposed of properly), the sludge goes into the receiving stream.  Tr. July 18, 2006, at 96.
242. WP Sanitary discharges to “an unnamed tributary to the Susquehanna River” (Tr. July 18, 2006, (Holmes) at 94).  Therefore, Mr. Kresge’s assessment that “his” sludge is in Harrisburg is a probable observation.

243. WP Sanitary’s certified operator is Joseph Bontrager.  Tr. July 18, 2006, at 61.

244. Joseph Bontrager oversees operation of WP Sanitary wastewater treatment plant.  Tr. July 18, 2006, at 61.

245. Joseph Bontrager is not based at WP Sanitary; he lives in Clarks Summit.  He may be at WP Sanitary on weekends for about three (3) hours; if needed he may be at the plant during the week.  Tr. July 18, 2006, at 61.

246. During his site inspection on March 8, 2006, Mr. Fought, an expert witness for the OCA, noted an improper roll in the old and new treatment plant aeration tanks.  OCA Statement No. 1 at 12.
247. During his site inspection on July 17, 2006, Mr. Fought noted an improper roll in the old treatment plant aeration tank.  Tr. July 18, 2006, at 147-148.

248. During Mr. Holmes’ site visit on July 17, 2006, he observed that incoming flow was still not equally distributed to the two splitter boxes.  Tr. July 18, 2006, at 81.

249. During Mr. Holmes’ site visit on July 17, 2006, the screen shown in Holmes Exhs. 4-2, 4-17, and 4-18 and Kresge Exh. K-3 was not on the splitter boxes.  Tr. July 18, 2006, at 81.

250. The treatment plant has no operational flow meter.  (Tr. July 19, 2006, at 172-175, and July 18, 2006, at 97-98.)  The existing flow meter is only installed to measure one of the two treatment plant trains.  Tr. July 19, 2006, at 173, and July 18, 2006, at 97-98.
251. In a properly operating treatment plant, solids are settled out from the liquid sewage and deposited in sludge holding tanks on a daily basis, dried and hauled away as necessary.  Tr. July 18, 2006, at 46, 97, and 148.
252. Only suspended solids, that is, solids held in suspension, can be lawfully discharged from a treatment plant.  Normal discharges are clear.  Tr. July 18, 2006, at 86-87.
253. The WP Sanitary plant discharge to the receiving stream does not meet its NPDES
 permit.  Tr. July 18, 2006, at 88, 101-102; Schedule TLF-6.
254. Suspended solids are measured by weight, while settle-able solids are measured by biometrically determining how fast the solids settle.  WP Sanitary’s NPDES permit addresses suspended solids.  Tr. May 23, 2006, at 215.

255. If WP Sanitary properly met its NPDES permit, one would not see solids in the receiving stream.  Tr. May 23, 2006, at 211, 216.

256. Even if the receiving stream were dry upstream of the WP Sanitary discharge pipe, there would not be a build up of solids in the receiving stream, if WP Sanitary met its NPDES permit.  Tr. May 23, 2006, at 215.

257. WP Sanitary currently has no valid NPDES permit because DEP will not renew it due to compliance issues.  

258. Complainant Sylvester complained of a pungent smell outside her home for a few days during the summer of 2005, which she believed to be coming from the wastewater treatment plant.  Tr. February 27, 2006, at 89-90.
259. Complainant Finkler complained of a bad, potent smell coming from the direction of Debbie Drive and, specifically, the dirt road leading from there.  He first noticed the smell in the summer of 2005 and continued to smell it as of the date of the hearing.  Tr. February 27, 2006, at 128-130.  

260. Mr. Holmes’ testimony and that of the Complainants revealed that WP Sanitary is not managed and/or operated facility properly.

261. The cost of the necessary wastewater system improvements are considerable.  OCA Statement No. 1 at 18, Schedule TLF-10 at 3.
262. Utility customer rates include fees for reasonable operation and maintenance expenses and depreciation on plant in service.  Tr. July 18, 2006, (Fought) at 206, July 19, 2006, (Kresge) at 105, 121-122, 130.

263. It is unlikely that the Kresges or the Companies could obtain outside financing.  Schedule TLF-5; Tr. July 19, 2006, (Kraus) at 118-119.
264. Even with financing, it is unlikely that the Companies could make the investment necessary to provide adequate service while maintaining reasonable rates for service.  Tr. July 19, 2006, at 120-122.
265. Mr. Kresge is not credible.

266. Mrs. Kresge did not testify.

267. The management practices of the Kresges show that neither Carl nor Sandra Kresge can properly manage and/or operate a water supply utility or wastewater treatment utility.
268. Carl and Sandra Kresge are individually and collectively incapable of managing either a water supply utility or a wastewater treatment utility.

269. According to WP Water Company’s 2005 Annual Report, the value of the water company was $61,958.  Exhibit PS-4 at 15.

270. According to WP Sanitary Company’s 2005 Annual Report, the value of the sanitary company was $35,218.  Exhibit PS-7 at 13.
IV.
DISCUSSION TC "IV.
DISCUSSION" \f C \l "1" 
A.
Issues TC "A.
Issues" \f C \l "2" 
These formal complaints and the intervention of the PUC’s Law Bureau and the Office of Consumer Advocate (OCA) all relate to the complaints of the customers of WP Water and WP Sanitary and their ongoing service frustrations over numerous years.  The complaints regarding WP Water are lack of pressure, outages, the company’s consistent unresponsiveness, cloudy water, and sediment.  Regarding WP Sanitary, the complaints are the comprehensive failure of the Company to provide safe, adequate, reasonable, and efficient service, sewage backups, failure to maintain sanitary mains, tree blockages, and causing foul odors in the community.  Two of the formal complainants specifically ask that the Commission “shut the company down” or take the company away from the Kresges.  One complaint stridently asks that the Kresges be forbidden from operating any company “that has to do with public safety.”  A separate issue is the Kresges’ ignoring a Commission Order to provide metered service.
The corporate entities WP Water and WP Sanitary comprise Carl Kresge and his wife Sandra.  If any of the other named individuals that appear on the corporate filings have any day-to-day responsibilities in the management of the Companies, Mr. Kresge did not so indicate and the Parties in this case did not show it.  Specifically, Carl Kresge testified under oath that he did all of the operational aspects of the Companies and that Sandra did the bookkeeping and administrative duties.  (Tr. July 18, 2006, at 59.)  Sandra Kresge, the purported owner of the Companies, did not testify at all. 
The Kresges’ defense regarding the water complaints are that no one would provide them funding so that they could upgrade the system, and that a DEP employee sabotaged their efforts to secure PENNVEST funding.  Their defense to the wastewater complaints is that DEP would not help them remodel their plant, that their customers flush improper materials, and that customers will not remove problematic trees (roots infiltrating WP Sanitary’s lines).  The Kresges appear to accept no responsibility for the issues that have caused these formal complaints against WP Water and WP Sanitary.  
B.
Principles of Law TC "B.
Principles of Law" \f C \l "2" 
1.
Burden of Proof TC "1.
Burden of Proof" \f C \l "3" 
The proponent of a rule or order has the burden of proof.  66 Pa. C.S. § 332(a). Therefore, the complainants in this proceeding bear the burden of proving their case(s).  The complainants must show that the Companies are responsible or accountable for the problems described in their formal complaints in order to prevail.  Patterson v. Bell Telephone Company of Pennsylvania, 72 PA PUC 196 (1990); Feinstein v. Philadelphia Suburban Water Company, 50 PA PUC 300 (1976).  This must be shown by a preponderance of the evidence.  Samuel J. Lansberry, Inc. v. PA PUC, 578 A.2d 600 (1990), alloc. den., 602 A.2d 863 (1992).  That is, by presenting evidence more convincing, by even the smallest amount, than that presented by the other party.  Se‑Ling Hosiery v. Marqulies, 70 A.2d 854 (1950).  Additionally, any finding of fact necessary to support the Commission’s adjudication must be based upon substantial evidence.  Edan Transportation Corp. v. PA PUC, 623 A.2d 6 (1993); 2 Pa. C.S. § 704.  More is required than a mere trace of evidence or a suspicion of the existence of a fact sought to be established.  Norfolk and Western Ry. v. PA PUC, 413 A.2d 1037 (1980); Erie Resistor Corp. v. Unemployment Compensation Bd. of Review, 166 A.2d 96 (1960); Murphy v. Commonwealth, Dep’t. of Public Welfare, White Haven Center, 480 A.2d 382 (1984).

2.
Statutory Obligations TC "2.
Statutory Obligations" \f C \l "3" 
Section 1501 of the Public Utility Code states:
Every public utility shall furnish and maintain adequate, efficient, safe, and reasonable service and facilities, and shall make all such repairs, changes, alterations, substitutions, extensions, and improvements in or to such service and facilities as shall be necessary or proper for the accommodation, convenience, and safety of its patrons, employees, and the public.  Such service also shall be reasonably continuous and without unreasonable interruptions or delay.  Such service and facilities shall be in conformity with the regulations and orders of the commission.  Subject to the provisions of this part and the regulations or orders of the commission, every public utility may have reasonable rules and regulations governing the conditions under which it shall be required to render service. 
66 Pa. C.S. § 1501

The statutory and regulatory schemes allow great latitude in the methods companies can use to achieve the above requirements.  However, pursuant to section 3301 of the Public Utility Code, failure to achieve these obligations can result in the assessment of a civil penalty.  Section 3301 states:
(a)
If any public utility, or any other person or corporation subject to this part, shall violate any of the provisions of this part, or shall do any matter or thing herein prohibited; or shall fail, omit, neglect, or refuse to perform any duty enjoined upon it by this part; or shall fail, omit, neglect or refuse to obey, observe, and comply with any regulation or final direction, requirement, determination or order made by the commission, or any order of the commission prescribing temporary rates in any rate proceeding, or to comply with any final judgment, order or decree made by any court, such public utility, person or corporation for such violation, omission, failure, neglect, or refusal, shall forfeit and pay to the Commonwealth a sum not exceeding $1,000, to be recovered by an action of assumpsit instituted in the name of the Commonwealth.  In construing and enforcing the provisions of this section, the violation, omission, failure, neglect, or refusal of any officer, agent, or employee acting for, or employed by, any such public utility, person or corporation shall, in every case be deemed to be the violation, omission, failure, neglect, or refusal of such public utility, person or corporation.


(b)
Each and every day's continuance in the violation of any regulation or final direction, requirement, determination, or order of the commission, or of any order of the commission prescribing temporary rates in any rate proceeding, or of any final judgment, order or decree made by any court, shall be a separate and distinct offense.  If any interlocutory order of supersedeas, or a preliminary injunction be granted, no penalties, shall be incurred or collected for or on account of any act, matter, or thing done in violation of such final direction, requirement, determination, order, or decree, so superseded or enjoined for the period of time such order of supersedeas or injunction is in force.

(Emphasis added.)  
66 Pa. C.S. § 3301

Before a utility begins operation, typically, the utility must seek a certificate of public convenience, or license to operate.  To receive such authority to operate, a utility’s first obligation is to demonstrate that they have the technical and financial capacity to operate in accordance with the Public Utility Code (“Code”).  The statutory and regulatory scheme exists in part to protect the public.  Succinctly stated in Commission policy, “A viable water system is one which is self-sustaining and has the commitment and financial, managerial and technical capabilities to reliably meet Commission and Department of Environmental Resources (Department) requirements on a long-term basis.”  52 Pa. Code § 69.701 (a)(2).
C.
Complaints Against WP Water TC "C.
Complaints Against WP Water" \f C \l "2" 
The Commission’s standard for determining whether water service is safe and adequate in accordance with 66 Pa. C.S. § 1501 was set forth in Pa. P.U.C. v. Pennsylvania Gas and Water Co. concisely, as “every customer is entitled to water that is fit for the basic, domestic purposes (e.g. cooking, drinking, washing and bathing).”  61 PA PUC 409, 416 (1986) TA \l "Pa. P.U.C. v. Pennsylvania Gas and Water Co.,  61 PaPUC 409, 74 PUR4th 238 (1986)" \s "Pennsylvania Gas and Water Co  74 PUR4th 238, 245 (1986)" \c 8 .  Additionally, regulations set forth the minimum requirements for water pressure, which require WP Water to maintain normal operating pressures of not less than 25 pounds per square inch (psi) and not less than 20 psi during periods of peak seasonal loads at the time of hourly maximum demand.  52 Pa. Code § 65.6(a).  DEP regulations parallel this requirement at 25 Pa. Code § 109.607 (b).  

1.
Low Water Pressure and Outages TC "1.
Low Water Pressure and Outages" \f C \l "3" 
Complainant Sylvester testified her water pressure is lower before and after work, on weekends and in the spring and summer.  Complainant Finkler testified that his water pressure is constantly low.  Complainant Sylvester additionally testified that during the summer of 2005, her water pressure was the worst she had experienced.  She stated:
Friday nights, there is no taking a shower.  Saturday, as long as you get up early in the morning, and I mean early, 4:30, 5:30 in the morning to take a shower or if I need my hair washed...And by Sunday I have no water.  This went on all summer in 2005.  There was no water.  It was every Sunday you had to go out to eat or cook on the grill.  There was nothing to be used in the house everything had to be paper products because you couldn’t wash it…we could, early in the morning Monday, take a shower.  Tr. February 27, 2006, at 32.  
According to the complainants, periods of low pressure became increasingly severe over the years.  (Tr. February 27, 2006 at 30, 32, 58, 61.)  Complainant Sylvester testified that in earlier years, she only had low pressure problems on holidays or other days when many customers were at home and using larger than usual quantities of water.  However, she testified “[n]ow it’s all the time.”  (Tr. February 27, 2006, at 61-62 and Tr. February 27, 2006, (Finkler) at 106, 111.)
WP Water customers endure frequent water outages.  Lengthy outages occurred in summer 2005, October 2005 and July 2006.  (Tr. February 27, 2006 (Sylvester) at 36-37, 73, (Finkler) at 101-02, 111, Tr. July 19, 2006 (Lash) at 24, 26, 55.)  Complainant Sylvester estimated that she lost all water service twice each year for periods lasting from one day to three or four days.  During such outages, the WP Water customers must buy water elsewhere to meet their household needs.  Consequently, the customers pay doubly; first, they pay WP Water for a service not received, and secondly, they must purchase the necessary water elsewhere.
Moreover, the Complainants never received notice from WP Water before an outage would occur.  A utility company is required to (1) keep a record of each prolonged interruption of service affecting its entire system or part of its system (52 Pa. Code §65.5 (a)); (2) make scheduled interruptions at hours that will provide the least inconvenience to its customers 52 Pa. Code § 65.5 (b); and (3) adopt a number of steps to notify the Commission of unscheduled service interruptions.  52 Pa. Code § 67.1 (a)-(e).  WP Water has not complied with these requirements.  Despite no party providing test results for pressure, or psi, it is clear that on the occasions when customers had no water at all, sometimes for days, that WP Water was not meeting the 25 psi regulatory requirement.  The customer complaints regarding low water pressure and outages were corroborated by expert testimony and facts in the record, were acknowledged by the Company, and were stipulated to in the Stipulated Findings of Fact.  (Exh. KS-6; see also Tr. July 19, 2005 (Kresge) at 179; St. K-8 at 5; St. K-9 at 2-3.)
The experiences of Complainants Sylvester and Finkler constitute inadequate and unreasonable service.  Due to low water pressure, WP Water customers are frequently unable to take showers, do laundry, and wash dishes or flush toilets.  This means that the service provided by WP Water is not fit for basic domestic purposes and thus, constitues inadequate service.
The following Commission policy guidelines related to unscheduled water service interruptions became effective December 16, 2006, and are relevant to the experiences of the WP Water customers.
§ 69.1601. General.
(a)
The purpose of this statement of policy is to provide guidance to the water industry relating to unscheduled water service interruptions, particularly regarding the types of public notice and associated actions that will be deemed acceptable and appropriate for meeting the safe, reasonable and adequate standard in 66 Pa. C.S. § 1501 (relating to character of service and facilities) and for complying with the Commission’s regulation in § 56.71 (relating to interruption of service).  It is imperative that affected ratepayers/occupants receive actual, timely and sufficient notice of unscheduled service interruptions whenever a situation affects water quality or quantity and particularly when the water is unsafe to drink. 
(b)
Affected ratepayers/occupants should be notified when 2,500 or 5%, whichever is less, of a utility’s total ratepayers/occupants have an unscheduled service interruption involving any reduction in the quantity of water in a single incident of 6 or more consecutive hours.  Timely notification of fewer customers, however, is recommended when practicable.  When there is an unscheduled service interruption involving the quality of water, water utilities should follow the applicable Department of Environmental Protection regulations regarding the public notification requirements for events requiring Tier 1 notification under 25 Pa. Code § 109.408(b) (relating to Tier 1 public notice—form, manner and frequency of notice), or Tier 2 notification under 25 Pa. Code § 109.409(b).  Timely notification of customers in other incidents affecting the quantity or quality of water, such as water in short supply, discolored or sediment-laden, however, is recommended when practicable.  It is also recommended that utilities set as a goal the Tier 1 time frame of “as soon as possible” rather than “no later than 24 hours” and the Tier 2 time frame of “as soon as possible” rather than “but no later than 30 days.” 
(c)
This statement of policy should not be considered to modify or replace in any way the public notice requirements of the Department of Environmental Protection found in 25 Pa. Code §§ 109.407-109.416 (relating to public notification.)
§ 69.1602. Public notification guidelines.
(a)
In the event of an unscheduled water service interruption, the following acceptable methods of public notification should be considered and utilized as appropriate: 


(1)
Fax/e-mail notification to local radio and television stations, cable systems, newspapers and other print and news media as soon as possible after the event occurs.  The notification must provide relevant information about the event, such as the affected location, its potential impact including possible adverse health effects and the population or subpopulation particularly at risk, and a description of actions affected ratepayers/occupants should take to ensure their safety, with updates as often as needed. 

(2)
Use of the utility’s own Internet website and 24/7 emergency phone line and integrated voice response system to provide relevant information about the event, such as the affected location, its potential impact including possible adverse health effects and the population or subpopulation particularly at risk, and a description of actions affected ratepayers/occupants should take to ensure their safety, with updates as often as needed. 

(3)
Automated dialer system (outbound dialing) notification to affected ratepayers’/occupants’ landline or wireless phones. 

(4)
Actual notice to affected health care and child care facilities and other facilities, for example, schools and restaurants, as determined by consultation with the Department of Environmental Protection, the Department of Agriculture, the Department of Health, the Department of Aging and other State agencies as necessary. 

(5)
Other types of direct or actual notice, such as doorknob flyers distributed to affected ratepayers/occupants, when feasible. 

(6)
E-mail and text message notification to affected customers who have opted to receive notice through use of these methods. 

(7)
Coordination with State and local emergency management agencies as needed to use the emergency alert system for qualifying situations. 
(b)
Utilities should have public notice templates prepared in advance to be available when needed to avoid wasting critical time developing materials when confronted with an unscheduled service interruption.  The notices should cover all possible scenarios from water conservation to boil water alerts to contaminants of concern and associated health effects.  Smaller utilities can look to resources that are available on the websites of the Department of Environmental Protection, the United States Environmental Protection Agency, the Pennsylvania Section of the American Water Works Association and the Pennsylvania Chapter of the National Association of Water Companies for assistance in developing public notice templates. 
(c)
To ensure that the public is informed, utilities should have a knowledgeable contact person stationed onsite during the emergency, if possible, to communicate to the public and media on behalf of the company.
§ 69.1603.  Other associated actions.
(a)
Water utilities need to make reasonable efforts to ensure that adequate quantities of alternative supplies of water essential for domestic use are made available in a sufficient number of conspicuous and predetermined locations relative to the number of ratepayers/occupants affected by the incident.  This includes the use of water tankers or free bottled water, or both.  Utilities should ensure that ratepayers/occupants are adequately notified of the times available and locations of alternative water supplies.  When bottled water is used, utilities should have plans in place, based on prior coordination with local vendors, to have adequate supplies to last for the duration of the outage.  The Commission encourages utilities to work proactively with community-based organizations that would have readily available information on the location and special needs of affected elderly or homebound ratepayers/occupants in the area. 
(b)
Notice should be made to Commission personnel as soon as possible upon a utility becoming aware of an unscheduled service interruption.  It should be noted that § 67.1(c) (relating to general provisions) already directs utilities to contact the Commission within 1 hour following preliminary assessment of conditions.  Furthermore, jurisdictional utilities should maintain lists of appropriate Commission contact personnel, including current after-hour contact numbers.

2.
Inadequate Supply and Storage TC "2.
Inadequate Supply and Storage" \f C \l "3" 
Mr. Fought, an expert witness testified on behalf of the OCA.  He earned a Bachelor of Science in Civil Engineering and practices as a Professional Engineer.  Mr. Fought explained that the primary cause of low pressure and outages is that WP Water does not have sufficient water sources to consistently meet its water demands.  WP Water’s three wells produce a safe yield of 31 gallons per minute.  The average daily water demand on the system is approximately 20.14 gallons per minute.  The water system’s maximum day demand is estimated to be 36.25 gallons per minute.  The wells may meet demands on a given average day, but the wells cannot meet peak demands.  During peak demands, customers at higher elevations do not receive adequate pressure and flow.  Under the DEP’s formula for calculating the system’s “safe yield,” not even the average daily water demand can be met.  The topography of the Washington Park service area is not level.  Complainant Sylvester and Complainant Finkler are two of the customers who reside at higher elevations in Washington Park.  In general, the higher elevations in the development are to the west and to the north.  Water pressure varies inversely with pipe elevation, such that customers who reside at lower elevations on the system have greater water pressure than customers who reside at higher elevations.  
Mr. Kresge, regarding adjusting the system pressure with a transducer, stated “I feel it’s going to make a marked difference with Mrs. Sylvester’s pressure area and any of the higher elevations that have had pressure problems there before that I’ve been so concerned about since 1993.”  (Tr. July 19, 2006 at 179.)  But WP Water lacks sufficient finished water storage overall, so even if pressure is addressed, the problem of simply not having the water still persists.  Mr. Fought explained that the system should have at least 7,380 gallons to 15,660 gallons of finished water storage.  WP Water has only one 3,000 gallon tank.  A 3,000 gallon hydro-pneumatic tank actually contains less than 3,000 gallons of water because air takes up part of the volume.  It is not in dispute, that WP Water has less than half of what is needed to service its paying customers.  This state of affairs did not occur spontaneously.  The situation at WP Water is one that Mr. Kresge knew of (or should have known of) early on in his tenure as its president.  In spite of obvious indications that the water system could not take on new customers, the Kresges continued to add new customers.  Aside from that, if WP Water had additional storage, it would likely have reduced the severity or duration of its customers’ recent outages.
The October 2005 outage occurred because one well was being repaired when a second well failed.  In July 2006, WP Water’s electric utility experienced a power outage and because WP Water has no back up generation equipment in service, customers were without water for more than eleven hours.  The Companies have backup electric generation equipment that Mr. Kresge asserted is available; however, the equipment is not kept at the WP Water plant, and this same equipment is the backup for all of the Kresge enterprises.  If this equipment is needed elsewhere, then the WP customers have no backup.  It is unreasonable that WP Water does not have dedicated generator backup for their customers.  It is unreasonable that the Kresges presume one generator can reasonably provide backup for their numerous enterprises.
If WP Water had the recommended volume of water storage during these outage incidents, the stored water would have helped to meet customer needs.  Mr. Kresge agreed that the system needs additional storage “to provide increased water pressure on a more consistent basis to its customers.”  One cannot help but wonder why Mr. Kresge did not arrive at that conclusion years earlier and set aside a portion of the collected tariff to work toward that goal.  In the decades that the Kresges have owned and operated WP Water, a portion of the tariff was intended to be used for maintenance of the facility.  The Kresges did not adequately do this.
3.
Metering TC "3.
Metering" \f C \l "3" 
WP Water customers’ usage is not metered and customers are charged flat rates of $38.25 for water and sewage service.  In its Order at Docket No. M-820308, entered April 26, 1991, the Commission directed WP Water to “provide metered service to [its] 52 customers…no later than March 1995” and directed the Company to “meter all new residential, commercial and industrial customers as their respective services are connected.”  The April 1991 Order was the Commission’s response to a proposed metering plan submitted by WP Water on July 25, 1990.  The metering plan was filed with the Commission pursuant to 52 Pa. Code § 65.7 that states:  “a public utility shall provide a meter to each of its water customers…
” The Order noted that WP Water had stated it needed a year to meter its system after a PENNVEST loan was secured.  The Order was issued in 1991 and granted WP Water not the one year requested, but rather, four years to meet the metering mandate for its 52 customers.  The Order was not contingent upon a PENNVEST loan.  Metering is a universal requirement that all water utilities have been required to meet.  See 52 Pa. Code § 65.7(a)-(d).  Not only did the Kresges ignore the Order regarding metering of their (then) 52 customers, but they connected 100 or more new customers without metering them, after the Commission’s Order to meter all new connections.  PUC witness Larry Lash explained that Commission staff likely did not become aware of the violation of the order because WP Water has not filed a rate case since the metering Order was entered.
Compliance with the Commission Order, by installation of the ordered meters and implementation of metered rates might have encouraged WP Water customers to conserve their water.  Customers who have water pressure can water their lawns and gardens, fill pools, wash cars and perform other nonessential usage chores.  Metering facilitates customers’ awareness of their own consumption.  Metering might have helped the higher elevation customers have pressure for their daily essential household needs, and it might have helped address WP Water’s perennial pressure problems.  Metered rates can be implemented without a revenue increase, through a revenue-neutral rate filing.  Metering will not eliminate WP Water’s pressure problems because the Company simply has woefully insufficient supply and storage as explained above, but metering could have supported a better water supply had the Kresges chosen to comply with the Commission’s Order.  WP Water’s inadequate storage situation must be resolved.  To that end, WP Water agreed at hearing that meters should be installed for all customers.  Such agreement in 2006, after more than a decade
 of ignoring a Commission Order, is of little use to the customers who have continued to pay the tariff every month. 
Unilaterally, the Kresges decided they would not comply with the Commission’s April 1991 Order.  The Kresges chose to ignore the Order rather than enter a discussion with the Commission or the Commission’s Fixed Utility Services staff.  The appropriate way for the Kresges to have handled the directives of the Order, if they anticipated trouble complying, was to request a stay of its obligations pending discussions with staff as to how to accomplish the directives and how to provide adequate service to the customers.  The Commission routinely works with utilities of all types in joint efforts to provide service that meets the mandates of the Public Utility Code.  It is likely that the Kresges did not approach the Commission for either a rate increase or assistance deliberately to avoid attention to themselves and the various Company issues.  The Commission cannot be everywhere, and it is not intended to be.  The Code and regulations presume lawful compliance.  The burden is on an owner and operator to know the applicable laws and to comply.  Here, the Kresges chose to willfully ignore a Commission Order and avoid detection of the violation as long as possible.  The Kresges’ poor management decisions ensured that the inadequate service to the WP Water customers would be perpetuated.

There are two components to the WP Water and Kresges’ violation of the April 1991 Order.  The first is the violation of Paragraph 2 of the Order that required WP Water to meter its then 52 customers by March 1995.  That violation subjects WP Water to a civil penalty.  The second component is the violation of Paragraph 3 of the Order that directed WP Water to meter all new residential, commercial, or industrial customers as their respective services were connected.  Under the directives of the Order, WP Water was not to connect any new users unless and until they were metered.  At the time of these hearings, eleven years later, no WP Water customers were metered.  All customers still pay flat rates for service.  Thus, all connections made subsequent to the April 1991 Order without being metered constitute a violation of the Order that subjects WP Water to a civil penalty.  A civil penalty for these violations will be addressed separately below.
4.
Small Diameter Delivery Pipes TC "4.
Small Diameter Delivery Pipes" \f C \l "3" 
WP Water’s small diameter delivering pipes servicing most WP customers contributes to the Company’s pressure problems.  Pipe diameter is inversely related to pressure loss due to friction.  As the OCA witness, Mr. Fought explained, pressure loss is greater in smaller diameter pipe, which is one reason the Commission requires replacement mains to be no less than 6 inches in diameter.  “The distribution system shall be of adequate size and so designed in conjunction with related facilities as to maintain the minimum pressures required by § 65.6 (relating to pressures).  Pipe of a diameter of less than 6 inches shall not be used for distribution mains except in cul-de-sacs where the mains are not subject to being extended and are not more than 250 feet in length.”  52 Pa. Code § 65.17.  Depending on the flow rate, the friction loss in a 3-inch diameter pipe is approximately 25 to 30 times greater than the friction loss in a 6-inch diameter pipe for the same flow rate.  Approximately 23% of the WP customers are served by 2-inch diameter pipe, 24% by 3-inch diameter pipe, 15% by 4-inch diameter pipe and 38% by 6-inch diameter pipe.  

WP Water’s inadequate pressure is exacerbated by allowing additional homes to be connected to the system.  At least twenty new homes were added since 1993 and new homes are currently being built.  It is anticipated that the new homes will hook up.  Mr. Kresge gave no indication the Company intended to block any new paying customers regardless of impact on current users.  The regulations provide that a utility company has the authority to decline to hook up additional customers when the company determines that to do so would be detrimental to the company.  Indeed, based on the lack of pressure, outages, and need for updating infrastructure, WP Water was obligated to deny new service pursuant to section 65.15 that states:
A public utility may decline to serve an applicant if it does not have adequate facilities to render the service desired or if such service is of a character that it is likely to have a detrimental effect upon service to other customers.  (Emphasis added.)  52 Pa. Code § 65.15 (b)

Section 65.17 states:
The quantity of water delivered to the distribution system from total source facilities should be sufficient to supply adequately, dependably and safely the total requirements of all customers under maximum consumption and should be determined so as to maintain the specified pressures as required by § 65.6.  (Emphasis added.)  52 Pa. Code § 65.17
The substantial evidence provided in these proceedings demonstrated that WP Water has not had sufficient storage capacity to provide adequate, dependable service to its customers in many years.  WP Water has always been in the best position to know the capacity of its own system.  Therefore, the Kresges, as the owner and president of WP Water, should have determined without any prompting by the PUC or DEP that adding additional customers to their already beleaguered system was likely to have a “detrimental effect upon service to other customers.”  In addition to failing to meet the above, Mr. Kresge gives no indication that the Company intends to deny service to the newly built homes that will need water service.  The record provides substantial evidence that WP Water does not provide safe, adequate, reasonable, or efficient service to its current customers.  This record further provides substantial evidence that the Kresges’, if allowed to, would continue their pattern of feckless management and service.

5.
Commission Precedent TC "5.
Commission Precedent" \f C \l "3" 
Low pressure has been a factor in findings of inadequate service in numerous PUC decisions.  Pa. P.U.C. v. National Utilities, Inc., 87 PA PUC 1 (1997) TA \l "Pa. P.U.C. v. National Utilities, Inc., 87 PaPUC 1 (1997)" \s "National Utilities, Inc., 87 PaPUC 1 (1997)" \c 8  (“NUI”); Zachary Ronald Matenkoski v. Kawon, Inc., 1994 Pa. PUC LEXIS 59 TA \l "Zachary Ronald Matenkoski v. Kawon, Inc., 1994 Pa. PUC LEXIS 59" \s "Kawon, Inc., 1994 Pa. PUC LEXIS 59" \c 8  (“Kawon”); Kessler v. Shickshinny Water Co., 1987 Pa. PUC LEXIS 237 TA \l "Kessler v. Shickshinny Water Co., 1987 Pa. PUC LEXIS 237" \s "Kessler ., 1987 Pa. PUC LEXIS 237" \c 8 .  In Leon R. Dongelewicz v. Oneida Water Co., the Commission found that the company was providing inadequate service based in part on customers’ receiving continuously low water pressure.  1994 Pa. PUC LEXIS 76 TA \l "Leon R. Dongelewicz v. Oneida Water Co., 1994 Pa. PUC LEXIS 76" \s "Oneida 1994 Pa. PUC LEXIS 76" \c 8 , 25 (“Oneida”).  Customers experienced frequent low pressure that caused difficulties in running household appliances, taking showers and flushing toilets.  Oneida at 6-8.  In Kawon, customers had to schedule their normal household activities, like showering and doing laundry, to accommodate low water pressure.  Kawon at 9-11.  In both Oneida and Kawon, the Commission found that service was inadequate for basic household purposes.  

In NUI, the TA \s "National Utilities, Inc., 87 PaPUC 1 (1997)"  Commission cited frequent outages as a factor leading to inadequate service.  NUI, at 4-7.  Water service in Oneida TA \s "Oneida 1994 Pa. PUC LEXIS 76"  was not fit for common domestic purposes when customers experienced frequent outages typically lasting three to four hours and occasionally lasting for days.  As in those cases, WP Water customers experience frequent lengthy water outages.
Mr. Fought identified the improvements necessary for WP Water to provide adequate pressure consistently to all customers, stating, “The necessary improvements consist of developing a new water well source, constructing a finished water storage tank, and installing customer water meters.”  WP Water applied for a PENNVEST loan to make each of these improvements and install a back-up electric generator in 1994 or there about.  The PENNVEST loan was never approved.  The record indicated that the decision makers at PENNVEST did not have confidence in the business dealings of the Kresges.  This is indicated in PENNVEST’s letter to the Kresges requiring certain information be submitted to PENNVEST by the Kresges.  PENNVEST was concerned about the Kresges commingling of monies between the several Kresge enterprises and various other concerns.  Whether the Kresges complied with the letter is not known, but the PENNVEST loan was never granted.  Mr. Kresge’s testimony regarding his PENNVEST application was disingenuous.  See also PA PUC v. Wilbar Realty Company, Inc. and Carl Kresge, President, Docket No. C-00957541 Order entered January 16, 1998.  In the January 1998 Order, the Commission ordered inter alia:  (i) improperly collected PENNVEST surcharges refunded, (ii) separate banks accounts established to provide appropriate segregation of funds, (iii) staff to be hired to properly manage customer complaints, (iv) install meters and hire meter readers, (v) sanitize its mains, (vi) Wilbar Realty, Inc. to pay a civil penalty of $1000, and (vii) Carl Kresge to pay a civil penalty personally of $6000.
The testimony provided by Complainants Finkler and Sylvester and the testimony and exhibits of Mr. Fought for the OCA and Mr. Lash for the PUC Bureau of Fixed Utility Services provided substantial evidence that WP Water is persistently in violation of 52 Pa. Code § 1501.  Violation of § 1501 subjects WP Water to a civil penalty.  Assessment of this civil penalty will be addressed separately below.
D.
Complaints Against WP Sanitary TC "D.
Complaints Against WP Sanitary" \f C \l "2" 
Complainant Pugh’s formal complaint addressed only the sewage treatment services.  Complainant Pugh did not complain about WP Water.  Therefore, Docket No. C‑20065849 should be dismissed and marked closed.  On October 13, 2005, Complainant Pugh’s basement was flooded with wastewater.  Complainant Pugh indicated that the quantity of sewage in his basement was more than the quantity of waste produced by his home alone.  He had a check valve on the service lateral entering his home.  The valve check did not stop the flow of wastewater into his basement.  It may not have been operating properly.  There was no rainfall in the days prior to Complainant Pugh’s basement being flooded.  Therefore, rain did not contribute to the quantity.
Complainant Pugh had raised concerns that tree roots were clogging WP Sanitary’s collection mains because the joints in the terra cotta (or vitreous clay) pipes were not properly sealed.  Complainant Pugh and his family check sewage flow levels in the manhole near his property on a frequent basis.  They lift the manhole cover and visually check the level.  When level is high, they move everything out of their basement because of their fear that sewage will back up into their home as it did in October 2005.  In 2005, Mrs. Pugh called Mr. Kresge numerous times to warn him that the sewage levels were rising.  Prior to a disagreement about responsibility for tree roots in the mains, the Kresges allowed the Pughs to call Roto-Rooter and request service.  After the disagreement, the Kresge and Pugh relationship was strained and the Pughs no longer called Roto-Rooter directly.  Now, when Mr. or Mrs. Pugh call, Mr. Kresge or his wife call Roto-Rooter to have blockages in the collection mains cleared.
1.
Blockages in Collection Mains TC "1.
Blockages in Collection Mains" \f C \l "3" 
The collection sewer mains installed in two or three streets, including Thomas Drive where Complainant Pugh lives, are made of vitreous clay with tar joints.  Tar joints are conducive to infiltration and inflow.  This is one reason that clay pipe with tar joints are no longer commonly installed in collection systems.  Instead, “O-ring” joints, with a tighter seal, have been commonly used for sanitary sewers since the late 1950’s, explained Mr. Fought.  
Mr. Fought concluded that backups were likely due to “a combination of the sewer system having excessive infiltration/inflow and partial blockage(s) in downstream sewers, possibly due to tree roots entering the pipes through joint openings and cracked pipes.”  Mr. Kresge confirmed, “the problem is clearly the fact that the roots from [the] trees are infiltrating the main line” and that he (Kresge) has to have tree roots cut out of the mains about every two years.  As Mr. Kresge stated, tree roots grow through the tar joints in the vitreous clay collection main, block the flow of wastewater and can cause wastewater to backup into customers’ service laterals.  Mr. Kresge testified that it was an ongoing problem.  This is consistent with Mr. Fought and Mr. Pugh’s assessment that the quantity of sewage that flooded Mr. Pugh’s home was indicative of a blockage in the collection main rather than the service lateral.  “[The sewage] would have been from his commodes, it would have been from his sink, it would have been from his shower.  It wouldn't have been from anybody else's and it would not have been the amount of water that was indicated by the damage that I saw.”  Customers located upstream of blockages in the Company-owned mains are subject to flooding if check-valves are not installed or do not operate.  It is the Company’s responsibility to remedy if a backup originates in the collection mains.   “The sewer company is responsible for correcting the excessive infiltration and inflow and blockages in sewer trunk lines and mains and also that portion of the customers’ house service laterals within the street curb lines.  The customer is responsible for blockages in the customer’s house service lateral, which extends from inside the customer’s home to the curb line.”  (WP Sanitary Tariff, original pp. 3-4; OCA St.1 at 16.)
Excessive infiltration/inflow can contribute to wastewater backing up from collection mains into customers’ service laterals.  The WP Sanitary system is subject to excessively high flows from infiltration/inflow.  Despite knowing of their infiltration/inflow issue, WP Sanitary has never obtained bids or cost estimates for an infiltration/inflow study.  Moreover, WP Sanitary already has the authority in its tariff to direct customers to disconnect any sump pumps and footer drains from the system, which contribute to a plant’s inflow.  Based on the dearth of management activities performed by the Kresges overall, it is unlikely that they performed any survey or inspection of their customers to determine who complied with the tariff and who did not.
Contrary to Mr. Kresge’s testimony, the solution for tree roots growing into the company collection mains is not to remove township trees.  As Mr. Fought explained:  the Company, not the tree owners, is responsible for having pipes that are able to deal with tree root infiltration.  Control of infiltration/inflow is part of the normal operation of any wastewater system.  (Tr. July 18, 2006 (Fought) at 166-68.)  
2.
Commission Precedent TC "2.
Commission Precedent" \f C \l "3" 
Where customers had instances of sewage backing up into their homes, and the backups were caused by blockages in the collection mains resulting from improper system maintenance on the part of the company, the company was found to have provided inadequate service.  Deresky v. Winona Lakes Util., Inc., 2000 Pa. PUC LEXIS 8.  (“Deresky”)   TA \l "Deresky v. Winona Lakes Util., Inc., 2000 Pa. PUC LEXIS 8" \s "Winona" \c 8 In addition to not maintaining its collection mains resulting in blockages, the company also failed to replace a company-owned faulty check valve.  In Deresky, the customers also had their own check valve, which they learned how to shut to avoid sewage flowing into their home.  However helpful Deresky may be, the utility company in that case did not present any evidence as was done here.  In Deresky, the utility lost the case by default because it failed to appear, and the complainant’s presentation of evidence was accepted without the utility being available for rebuttal.  In stark contrast, here, the parties agreed that the system is subject to excessive infiltration and inflow.  Mr. Fought recommended that WP Sanitary find the cause of excessive infiltration and inflow in the system.  That study will indicate to what extent the collection mains need to be rehabilitated in order to eliminate the excessive infiltration/inflow.  Mr. Fought anticipated that the study would support replacement of the vitreous clay mains.  WP Sanitary and its Certified Operator both agreed that the sources of excessive infiltration/inflow must be studied and corrected. 

Irrespective of such agreement, WP Sanitary took no steps to study the extent that its mains need rehabilitation and to eliminate the perennial infiltration and inflow problem.  It is also undisputed that tree roots in the collection mains create blockages, but WP Sanitary does not preventatively clear roots in the mains until after there is a blockage and sewage is backing up in the mains.  In addition to not maintaining its collection mains resulting in blockages, WP Sanitary failed to replace a company-owned faulty check valve.  The customers had their own check valve, which they learned how to shut to avoid sewage flowing into their home.  
3.
Severe Malodors TC "3.
Severe Malodors" \f C \l "3" 
Customers have experienced a pungent smell in the area surrounding the plant.  Complainant Sylvester complained of a pungent smell outside her home for a few days during the summer of 2005, which she believed to be coming from the direction of the wastewater treatment plant.  Complainant Finkler complained of a bad, potent smell coming from the direction of Debbie Drive and, specifically, the dirt road leading from there.  He first noticed the smell in the summer of 2005 and testified during hearing that the odor was still present.  

In addition to the customer complainant testimony, James Holmes, who holds a Bachelor of Science degree in Agriculture and a Master of Science degree in Microbiology, testified on behalf of the OCA.  Mr. Holmes has worked in the DEP’s water quality bureau since 1980 and, specifically, in DEP’s operations section dealing with water and wastewater plants since 1985.  As a field inspector and a supervisor, he has monitored WP Sanitary since 1986.  Mr. Holmes is a DEP Water Quality Specialist Supervisor.  He responded to a complaint regarding severe malodors near the WP Sanitary treatment plant on September 7, 2005.  Mr. Holmes personally detected the severe septic or rotten egg odor at the treatment plant and at the stream on September 8, 2005, and September 13, 2005.  Mr. Fought also testified that he experienced the smell at the treatment plant on July 17, 2006, and on March 8, 2006, when he first toured the plant.  Mr. Fought did not conclude that the detectable odor was coming from a farmer’s field, as claimed by Mr. Kresge.  
Both Mr. Fought and Mr. Holmes’s testimony showed that the unpleasant smells are a result of the poor operation and maintenance of WP Sanitary.  Moreover, in a properly managed and operated treatment plant, solids that can exacerbate odors, are settled out from the liquid sewage and deposited in sludge holding tanks on a daily basis, dried and hauled away as necessary.  No settle-able solids should be discharged from a plant.  Only suspended solids can be lawfully discharged (that is, in accordance with a valid NPDES permit) from a treatment plant.  By definition, suspended solids are not settle-able.  The liquid sewage then flows into a chlorine contact tank, where it is chlorinated and discharged.  

WP Sanitary is not properly treating its sewage for at least two reasons.  First, solids will not properly settle out unless there is a proper roll in the mixed liquor.  When the mixed liquor in the aeration (or settling) tanks does not have a uniform, even roll, it indicates improper aeration.  Mr. Fought noted an improper roll in the old and new treatment plant aeration tanks during his March 8, 2006 inspection.  According to WP Sanitary, by June 2006, it had repaired and replaced the blowers.  However, they only provided an invoice for two blowers which indicated the entire balance was still due.  No invoice or confirmation was provided to confirm the blowers had been repaired or replaced.  I cannot tell, therefore, if the blowers were replaced.  On July 17, 2006, the roll in the new treatment plant showed improvement; however, the old treatment plant was still operating poorly.  
When an aeration plant is not operated properly, the liquid can become septic.  Septic treatment plants have a strong hydrogen sulfide smell, similar to rotten eggs.  Mr. Holmes reported that on September 8, 2005, the plant effluent was septic.  
In addition to improper aeration, the treatment plant is designed to detain 35,000 gallons of mixed liquor for 24 hours.  As testified to by Mr. Kresge, each day, the plant experiences a peak flow rate that is greater than it can effectively treat.  And, as already noted, the system is subject to excessively high flows from infiltration/inflow.  According to WP Sanitary’s Certified Operator, Joseph Bontrager:  
There are several inherent problems with the working of the [WP Sanitary] sewer plant.  The largest problem is one of excessive inflow and infiltration (I&I).  The I&I is quite heavy during heavy rainfall events and rapid snow melt.  These events, if large enough, wash the activated sludge from the plant.  After these events, recovery of a healthy population of microbes for good treatment takes some time.

(Exh.TLF-10 at 3.)
When the flow into the treatment plant greatly exceeds its capacity, as described by Mr. Bontrager, sludge is washed straight through to the receiving stream without treatment.  “When it rains, the solids are being pushed through the treatment plant, pushed through the aeration tank, pushed into the contact tank and right into the stream.  The solids are just blowing right though the plant when it rains.  The infiltration is so high that the plant is not being able to assimilate the solids and the solids are just blowing out.”  Mr. Kresge’s own testimony corroborates Mr. Bontrager’s assessment.  Moreover, the pictures provided by Mr. Holmes provide the clearest evidence that sewage sludge and solids from WP Sanitary have indeed “blown right through” to the receiving stream.
Mr. Fought calculated that the treatment plant should produce about 22.3 pounds of dry sludge per day or 268 gallons per day of sludge containing 1% solids (typical for un-decanted sludge).  For every year that sludge is not hauled from the plant, the equivalent of 8,140 pounds of dry sludge or 97,820 gallons of sludge containing 1% solids are discharged into the receiving stream.  Waste sludge has not been hauled from WP’s treatment plant since at least 2001.  

There are large depositions of sewage sludge in the receiving stream.  However, Mr. Kresge agreed that when his customers paid their monthly sanitary bills, they were paying for the collection, cleaning, and proper discharge of the effluent, and proper hauling away of any sludge.  He agreed part of their money was to go toward operation and maintenance of the plant.    The Commission has stated:
It is our opinion that in exchange for the utility’s provision of safe, adequate, and reasonable service, the ratepayers are obligated to pay rates which cover the cost of service which includes reasonable operation and maintenance expenses, depreciation, taxes and a fair rate of return to the utility’s investors.  Thus, as the OCA contends, a quid pro quo relationship exists between the utility and its ratepayers.  

Pa. P.U.C. v. Pennsylvania Gas and Water Co., 61 PA PUC 409, 415-16, 74 PUR4th 238, 245 (1986) (PG&W).  
WP Sanitary’s failure to treat its customers’ sewage within the legal parameters is substantial evidence that they failed to provide the service for which WP Sanitary customers are paying.  Such incompetent operation and maintenance of a plant also accelerates the plant’s deterioration and will lead to an earlier need for replacement of a plant which can unreasonably increases costs to the ratepayers.

The record is replete with evidence that WP Sanitary is neither being operated properly nor maintained properly and that untreated sewage is discharged to the receiving stream.  Therefore, WP Sanitary is not providing safe, adequate or reasonable service to its customers and thus is in violation of § 1501 of the Code.  Such violation subjects WP Sanitary to a civil penalty, which will be addressed separately, below.
Mr. Fought made a number of long- and short-term recommendations that WP Sanitary agreed are necessary to improve operation of the treatment plant and to help address the complaints regarding malodors.  These same recommendations were made by WP Sanitary’s Certified Operator.  WP Sanitary agreed with each of Mr. Fought’s long-term recommendations.  Specifically, the Company agreed that the sources of excessive infiltration/inflow must be studied and corrected.  As part of the infiltration/inflow study, the Company agreed that a working flow meter should be installed, which measures both treatment plant trains.  The Company agreed that an equalization tank should be installed, with necessary DEP approvals.  The size of the equalization tank should be determined as part of an infiltration/inflow study.  Last, the Company agreed that tertiary treatment should be installed or the plant size should be increased, with necessary DEP approvals.  
With regard to Mr. Fought’s short-term recommendations, the Company agreed that the splitter box (diverter) should be replaced.  The Company provided some evidence to indicate that it has made repairs to its aeration system; however, Mr. Fought testified that aeration seemed improved, but not resolved.  In response, the Company agreed to adjust diffusers to improve aeration – and thus settlement of solids – in the treatment plant trains.  The Company also agreed that, during dry weather, the treatment plant tanks should be emptied, cleaned of sediment, repainted and repaired as necessary.  In addition, WP is currently in violation of its DEP permit because the plant is being operated without a comminuter.  Mr. Fought recommended that WP Sanitary install a comminuter or an automated bar screen, with necessary DEP approvals.  
E.
Civil Penalty TC "E.
Civil Penalty" \f C \l "2" 
1.
Civil Penalty Assessed Against WP Water TC "1.
Assessed Against WP Water" \f C \l "3" 
Section 3301 of the Code states:
(a)
If any public utility, or any other person or corporation subject to this part, shall violate any of the provisions of this part, or shall do any matter or thing herein prohibited; or shall fail, omit, neglect, or refuse to perform any duty enjoined upon it by this part; or shall fail, omit, neglect or refuse to obey, observe, and comply with any regulation or final direction, requirement, determination or order made by the commission, or any order of the commission prescribing temporary rates in any rate proceeding, or to comply with any final judgment, order or decree made by any court, such public utility, person or corporation for such violation, omission, failure, neglect, or refusal, shall forfeit and pay to the Commonwealth a sum not exceeding $ 1,000, to be recovered by an action of assumpsit instituted in the name of the Commonwealth. In construing and enforcing the provisions of this section, the violation, omission, failure, neglect, or refusal of any officer, agent, or employee acting for, or employed by, any such public utility, person or corporation shall, in every case be deemed to be the violation, omission, failure, neglect, or refusal of such public utility, person or corporation.  

(b)
Each and every day's continuance in the violation of any regulation or final direction, requirement, determination, or order of the commission, or of any order of the commission prescribing temporary rates in any rate proceeding, or of any final judgment, order or decree made by any court, shall be a separate and distinct offense.  [ ]
(d)
The amount of the penalty, when finally determined, may be deducted from any sums owing by the Commonwealth to the person or corporation charged or may be recovered in a civil action.  (Emphasis added.)  66 Pa. C.S. § 3301.  
WP Water is subject to a civil penalty for its failure to meet the requirements of Section 1501 of the Code.  While Mr. Kresge has stipulated to most of the facts that support a clear finding of this violation, it is necessary to identify some specifics.  Specifically, WP Water has failed to provide safe, adequate, reasonable and efficient service to it patrons by having persistently low water pressure and frequent outages (SFoF
 12-14, 17, 18, 23), by failing to provide water for basic household usages (SFoF 17, FoF 92), by utilizing undersized piping exacerbating poor pressure, and by failing to properly bill patrons (SFoF 1-3).  Additionally, WP Water is in violation of the Commission Order issued April 26, 1991, requiring the then current patrons to be metered and any new connections to be metered.
Commission standards for the application of a civil penalty were addressed in Joseph A. Rosi v. Bell-Atlantic-Pennsylvania, Inc. and Sprint Communications Company, L.P., Docket No. C-00992409 (Order entered March 16, 2000).  The Commission uses the standards developed in Rosi as a basis to develop the amount of civil penalties in cases regarding other utility issues.  Pennsylvania Public Utility Commission v. NCIC Operator Services, Docket No. M-00001440 (Order entered December 21, 2000).

The first standard to be considered is whether the violations were intentional or negligent.  If the violations were intentional, the Commission will start with the presumption that the penalty will be in the range of $500 to $1,000 per day.  If, on the other hand, the violation is negligent, the Commission will start with the presumption that the penalty will be in the range of $0 to $500 per day.  This first standard is generic in nature and can be applied to any utility type.  Mr. Kresge and his wife purchased WP Water approximately in 1985.  In that time, they have accumulated a long history of environmental violations with DEP and a lengthy history with the PUC for their recalcitrance toward achieving any meaningful level of compliance.  These violations are not the result of negligence.  The history and patterns of behavior are persistent and the violations are intentional.  I must also consider the length of time.  The statute of limitations provides that I can look retrospectively to the three years prior to the formal complaints being filed.  66 Pa. C.S. § 3314 (a).  Applying this, the civil penalty for violation of Section 1501 is 365 days, multiplied by three years.  At a daily penalty presumption of $500, the penalty is $547,500.
The next two standards are phrased in Rosi to address the issue of slamming; however, they may be used in other utility penalty cases beyond those involving slamming.  The second Rosi standard addressed the promptness with which the utility took steps to correct the issue, and the third Rosi standard questions whether the utility/Respondent initiated procedures to prevent the violation from occurring again.  WP Water, i.e., the Kresges took no meaningful actions to correct the violations or to prevent violation going forward.
The fourth and fifth Rosi standards question the number of customers impacted by the violations, and whether the recommended penalty arises from a settlement or a litigated proceeding.  The numbers of customers impacted by the Kresges’ deliberate poor management are approximately 150-152.  There has been no attempt at settlement.  
Standards six and seven question the compliance history of the utility, and whether the utility cooperated with the Commission in attempting to correct the problem.  WP Water has a history of failed compliance and has deliberately violated a Commission Order.  There has been no meaningful attempt by the Company to correct any problems.
The eighth and ninth standards consider the amount of a civil penalty necessary to deter future violations and considers past Commission decisions regarding similar issues.  The Company’s pattern of behavior is consistently recalcitrant, consistently unwilling to take responsibility, and unwilling to contact and work with the PUC staff, Mr. Kresge shows tendencies to treat the truth as malleable, and he deliberately obfuscates.  In my opinion, there is no additional penalty that will alter the pattern already demonstrated; therefore, I have not increased the base penalty of $500 per day.
The tenth Rosi standard is other relevant factors; none was considered.
Therefore, based upon the discussion of the Rosi standards, the penalty against WP Water for its compound violations of 66 Pa. C.S. § 1501 is $547,500.
2.
Civil Penalty Assessed Against WP Sanitary TC "2.
Civil Penalty Assessed Against WP Sanitary" \f C \l "3" 
WP Sanitary is separately subject to a civil penalty for its failure to meet the requirements of Section 1501 of the Code.  As with WP Water, Mr. Kresge has stipulated to most of the facts that support a clear finding of these violations.  Specifically, WP Sanitary has failed to provide safe, adequate, reasonable and efficient service to it patrons by failing to properly collect, treat and dispose of patrons’ sewage, and by failing to properly maintain the Company equipment and facilities, and by failing to properly enforce terms of the applicable tariff with regard to sump pumps and tree roots. (SFoF 26-46.)

Again, using the Rosi standards, the first standard to be considered is whether the violations were intentional or negligent.  I will not repeat my comments made above, as the same applies here.  WP Water and WP Sanitary are a tandem operation of the Kresges.  The history and patterns are the same.  Therefore, the civil penalty for WP Sanitary’s compound violations of Section 1501 is $500 multiplied by three years or $547,500.
The second Rosi standard addressed the promptness with which the utility took steps to correct the issue, and the third Rosi standard questions whether the utility/Respondent initiated procedures to prevent the violation from occurring again.  WP Sanitary, i.e., the Kresges, took no meaningful actions to correct the violations or to prevent violations going forward.

The fourth and fifth Rosi standards question the number of customers impacted by the violations, and whether the recommended penalty arises from a settlement or a litigated proceeding.  The numbers of customers impacted are approximately 150-152.  There has been no attempt at settlement.
Standards six and seven question the compliance history of the utility, and whether the utility cooperated with the Commission in attempting to correct the problem.  WP Sanitary has a history of failed compliance.  The Company had made no meaningful attempts to correct problems.
The eighth and ninth standards consider the amount of a civil penalty necessary to deter future violations and considers past Commission decisions regarding similar issues.  I addressed this above and need not repeat it here.

The tenth Rosi standard is other relevant factors.  I considered no additional factors.

Therefore, based upon the discussion of the Rosi standards, the penalty against WP Sanitary for its compound violations of 66 Pa. C.S. § 1501 is $547,500.

3.
Civil Penalty Assessed Against Carl Kresge TC "3.
Civil Penalty Assessed Against Carl Kresge" \f C \l "3" 
Section 3301 allows the imposition of a civil penalty against anyone who is subject to the statute stating at subsection (a):
In construing and enforcing the provisions of this section, the violation, omission, failure, neglect, or refusal of any officer, agent, or employee acting for, or employed by, any such public utility, person or corporation shall, in every case be deemed to be the violation, omission, failure, neglect, or refusal of such public utility, person or corporation.  66 Pa C.S. § 3301 
Subsection (b) provides:

Each and every day’s continuance in the violation of any regulation or final direction, requirement, determination, or order of the commission, or of any order of the commission prescribing temporary rates in any rate proceeding, or of any final judgment, order or decree made by any court, shall be a separate and distinct offense.

Subsection (d) provides:

The amount of the penalty, when finally determined, may be deducted from any sums owing by the Commonwealth to the person or corporation charged, or may be recovered in a civil action.
(Emphasis provided to show section application specific to Mr. Kresge.)
Pennsylvania law recognizes the participation theory as a basis of liability.  Simply stated, the participation theory provides:
[t]he general, if not universal, rule is that an officer of a corporation who takes part in the commission of a wrong by the corporation is personally liable; but that an officer of a corporation who takes no part in the commission of the wrong committed by the corporation is not personally liable to third persons for such a wrong, nor for the acts of other agents, officers or employees of the corporation in committing it, unless he or she specifically directed the particular act to be done or participated, or cooperated therein.  (Emphasis added.) 
3A Fletcher, Cyclopedia of the Law of Private Corporations § 1137, at 207, Perm. Ed. Rev. 1975.  See also: Chester-Cambridge B. & T. Co. v. Rhodes, 346 Pa. 427, 433, 31 A.2d 128, 131 (1943); Amabile v. Auto Kleen Car Wash, 249 Pa.Superior Ct. 240, 250, 376 A.2d 247, 252 (1977); Disco, Inc. v. Casper Corp., 587 F.2d at 606; Martin v. Wood, 400 F.2d 310, 312 (3d Cir.1968) (applying Pennsylvania law).

Liability under the participation theory attaches where the corporate officer is an actor who participates in the wrongful acts.  (Emphasis added.)  Corporate officers may be held liable for misfeasance.  Chester-Cambridge B. & T. v. Rhodes, 346 Pa. at 432, 31 A.2d at 131.  See also: Knuth v. Erie-Crawford Dairy Cooperative Ass'n., 463 F.2d 470, 481 (3d Cir.1972), cert. denied, 410 U.S. 913, 93 S.Ct. 966, 35 L.Ed.2d 278 (1973)  However, corporate officers and directors may not be held liable for mere nonfeasance.  (Emphasis added.)  Chester-Cambridge B. & T. v. Rhodes, 346 Pa. at 432, 31 A.2d at 131; Hager v. Etting, 268 Pa.Superior Ct. 416, 422, 408 A.2d 856, 859 (1979).  See also: Cohen v. Maus, 297 Pa. 454, 457, 147 A. 103, 104 (1929).
In this formal complaint proceeding, according to Mr. Kresge, he made all of the operational decisions; his wife Sandra handled the bookkeeping, billing, administrative, and office work.  Applying Pennsylvania’s participation theory, Mr. Kresge may be found personally liable if substantial evidence showed he was an actor participating in wrongful act(s).  

Under the participation theory, the court imposes liability on the individual as an actor rather than as an owner.  Such liability is not predicated on a finding that the corporation is a sham and a mere alter ego of the individual corporate officer.  Instead, liability attaches where the record establishes the individual’s participation in the tortious [wrongful] activity.  Wicks v. Milcozo Builders, Inc. 503 Pa. 614, A. 2d 86, 90 (1983)

A key to the application of the theory is whether the individual knew about the violations, but intentionally neglected to do anything about them.  Wicks at 90.  

WP Water has no board of directors; there is no management team or management company running WP Water.  WP Water is Carl and Sandra Kresge’s business, and a source of their income.  They have incorporated the company, but cannot stand behind the corporation laws to shield themselves from their personal misfeasance.  This is not a “piercing of the corporate veil” because; there is no need to do so.  That is precisely what the participation theory addresses.  Mr. Kresge is personally liable for his own misfeasance if he “knew about the violations, but intentionally neglected to do anything about them.”  Wicks at 90.  Mr. Kresge has the authority and the responsibility to meet the Code, regulations, and of course, the 1991 Commission Order.  There is no one in the chain of command higher than Mr. Kresge.  See Whitemarsh v. PADEP, 2000 EHB 300 (2000), Pa. Envirn. LEXIS 21.  

Mr. Kresge is personally liable because the record shows he knew of the 1991 Commission Order and (1) personally and deliberately chose not to comply with directives requiring metering.  Specifically and personally, Mr. Kresge had to agree to connect the approximately 100 users that were connected subsequent to the 1991 Order; no one else but Mr. Kresge had that authority and/or responsibility.  “She’s [i.e., Mrs. Kresge] not done anything of that nature.”  (July 18, 2006 at 59)   Mr. Kresge personally chose to not call or write to the Commission seeking advice on how to meet the directives when he personally realized meeting the directives was problematic.  It is not possible that the 100 additional customers could have connected to WP Water without Mr. Kresge’s specific authorization because, as he testified, he handles all the operational decision-making.  I can assume that Mr. Kresge discussed with Mrs. Kresge what the 1991 Order said and required, however I have no choice based on his own testimony, but to conclude that the ultimate decision to not seek PUC assistance and the ultimate decision to continue to hook up new customers was Mr. Kresge’s decision.  

The record is clear in the Commission Order that there were 52 users at the time the 1991 Order was issued.  There are approximately 152 now.  The additional 100 users were connected to WP Water with Mr. Kresge’s specific and personal consent.  His authorization for each new user to connect in violation of the 1991 Order was not simply negligence or nonfeasance.  Hooking up the approximately 100 additional users contrary to the Commission Order is clear as well as substantial evidence of misfeasance.  66 Pa. C.S. § 3301(a).  This conclusion is firmly supported by testimony and the stipulated facts.  See SFoF 11, 16, 17, 20, 21, 22.  For this misfeasance, a personal civil penalty applies.  The time of this personal violation is from March 31, 1995
 to the date of this decision.  For simplicity, no other reason, I will use the dates March 31, 1995 through July 31, 2007.  Applying the statute of limitations, I am again limited to reviewing and applying a civil penalty for three years or 1095 days.  66 Pa. C. S. § 3314 (a), (b).
Briefly restating the Rosi standards for determining an appropriate civil penalty, they are:  (1) intentional versus negligent; (2) promptness to correct; (3) preventative measures taken; (4) number of customers affected; (5) litigated or settled; (6) compliance history; (7) cooperation with the Commission; (8) deterrent factor; (9) similar Commission decisions; and (10) other relevant factors.  
Mr. Kresge’s misfeasance was intentional; he made no attempt to take corrective action by conferring with PUC staff; he took no preventative measures; approximately 100 customers were involved in the initial misfeasance, but, adding additional new users to the system affected the service of current users therefore, 152 were ultimately affected; this matter has been fully litigated and moreover, the 1991 Order was not appealed; Mr. Kresge’s two companies have an abysmal compliance history that can only be a personal reflection on himself as there is no one higher in the chain of command as stated earlier; Mr. Kresge has not attempted to cooperate with the Commission; I do not believe penalty will effectuate any change in Mr. Kresge’s set patterns of management and operations at both Companies; and no other relevant factors were considered.
Regarding similar decisions, (number 9 in the Rosi considerations), the most similar decision actually pertains to Mr. Kresge, and other supporting case law has already been cited above.  In PA PUC v. Wilbar Realty Co., Inc. and Carl Kresge, President, Docket C‑00957541 Order entered January 16, 1998, the Commission personally penalized Mr. Kresge $6000 for his using the corporate structure of Wilbar Realty to shield his wrongful conduct.  I believe an appropriate civil penalty against Mr. Kresge for his misfeasance is $100 per day, or $109,500.00 (3 years x 365 days x $100/day)  A lesser amount is not be appropriate due to Mr. Kresge’s callous disregard for his customers’ plights with their water service over the twelve (12) years and four (4) months since the Commissions Order.  
4.
Civil Penalty Assessed Against Sandra Kresge TC "4.
Civil Penalty Assessed Against Sandra Kresge" \f C \l "3" 
Sandra Kresge, (according to Mr. Kresge, because she did not testify, but did attend the hearings) is the owner of both Companies.  Also, according to Mr. Kresge, he operated the Companies; Mrs. Kresge did all of the bookkeeping, billing, office and administrative work.  Nonetheless, as the owner, Mrs. Kresge is personally responsible for the operation and maintenance of both Companies.  She is responsible for meeting the Code, Commission regulations, and Orders.  And, as explained in the citations and excerpts above, personal liability attaches due to one’s action(s), not one’s inaction(s).  
Mrs. Kresge’s personal liability for misfeasance regarding WP Water and WP Sanitary results from her failure to properly bill, failure to properly keep complaint records, and failure to provide proper boil water and/or outages notices.  These are three specific regulatory requirements that she personally had authority and responsibility for, she personally controlled, and she personally chose to violate.  Additionally, the April 26, 1991 Commission Order to WP Water was a requirement of Mrs. Kresge, however, I am not going to assess civil penalty for her personal violation regarding the 1991 Order, even though it is warranted because as the owner, Mrs. Kresge as well as her husband, had to personally choose to ignore the Commission’s Order.  Only because I have assessed a civil penalty against her husband for personal misfeasance regarding the Order am I declining to apply the same penalty against Mrs. Kresge.  I believe under the applicable law it does indeed apply to Mrs. Kresge with the same force and effect.  I simply choose to not apply it.  I am however, assessing civil penalty against Mrs. Kresge for her own behavior and misfeasance regarding her three (deliberately) miscarried administrative duties cited above.  As with her husband, the stipulated findings of fact support this conclusion as does testimony that evidenced failure to bill properly, failure to keep proper complaint records, and failure to issue proper notices.  See SFoF 1, 2, 3, 6, 7, 8, 9, 13, and 24.

After reviewing the Rosi criteria, the statute of limitations, and the explanations above about the history and patterns of the Companies (that apply to Mrs. Kresge equally as they do to Mr. Kresge), a civil penalty of $100 per day is appropriate, multiplied by three years of misfeasance amounting to a civil penalty of $109,500.00.
V.
CONCLUSIONS OF LAW TC "V.
CONCLUSIONS OF LAW" \f C \l "1" 
1. The Commission has jurisdiction over the parties and subject matter of this proceeding.  66 Pa. C.S. § 701.
2. The formal complainants and party intervenors have met their respective burdens of proof.  66 Pa. C.S. § 332 (a).

3. WP Water Company, Inc. and WP Sanitary, Inc. have failed to furnish and maintain adequate, safe, efficient, and reasonable service, and have failed to make all such repairs, changes, alterations, substitutions, extensions, and improvements in or to such service and facilities as shall have been necessary for the proper accommodation, convenience and safety of its patrons, constituting a violation of 66 Pa. C.S. § 1501.
4. WP Water, Inc. failed to:  (i) provide adequate storage capacity causing outages and pressure below the regulatory mandate; (ii) provide adequate notice of outages to patrons; (iii) provide water suitable for household purposes; (iv) install and implement meters and to charge metered rates; (v) provide adequate emergency backup electric generation.  66 Pa. C.S. § 1501.
5. WP Sanitary, Inc. failed to:  (i) provide proper collection, treatment, discharge, and disposal of patrons’ sewage and wastewater; (ii) make such necessary repairs and changes to the facility to accommodate patrons; (iii) correct excessive infiltration and inflow; and (iv) properly use the mandates of their own tariff to address tree roots, and sump pumps.  66 Pa. C.S. § 1501.
6. WP Water, Inc. is in violation of the Commission Order entered April 26, 1991, at Docket No. M-820308 requiring 52 customers to be metered “no later than March 1995,” for which a civil penalty applies.  52 Pa. Code § 65.7; 66 Pa. C.S. § 3301.
7. WP Water, Inc. is in violation of the Commission Order entered April 26, 1991, at Docket No. M-820308 requiring all new residential, commercial, and industrial customers to be metered upon connection.  52 Pa. Code § 65.7; 66 Pa. C.S. § 3301.

8. Carl Kresge and Sandra Kresge, jointly and individually do not possess the financial, managerial, or technical ability to operate a water utility or sewer utility.  66 Pa. C.S. § 529 (c) (1).

9. Violation of 66 Pa. C.S. § 1501 and failure to comply with a Commission Order subjects WP Water and WP Sanitary to assessment of a civil penalty.  66 Pa. C.S. § 3301.

10. Corporate officers may be held personally liable for their misfeasance.  Chester-Cambridge B. & T. v. Rhodes, 346 Pa. at 432, 31 A.2d at 131.

11. The personal and affirmative misfeasance of Carl Kresge subject him to a personal civil penalty.  66 Pa. C.S. § 3301, Wicks v Milzoco Builders, Inc., 503 PA 614, 470 A 2d 86, 89 (1983).

12. The personal and affirmative misfeasance of Sandra Kresge subject her to a personal civil penalty.  66 Pa. C.S. § 3301, Wicks v Milzoco Builders, Inc., 503 PA 614, 470 A 2d 86, 89 (1983).
13. Civil penalties assessed, if not timely paid, may be deducted from any sums owing by the Commonwealth to the person or corporation charged or may be recovered in a civil action.  66 Pa. C.S. § 3301(d).
VI.
ORDER TC "VI.
ORDER" \f C \l "1" 
THEREFORE,
IT IS ORDERED: 
1. That the formal complaints of Kathleen Sylvester at Docket No. C‑20055453, and William J. Finkler at Docket No. C-20055473, against WP Water Company, Inc. are sustained.

2. That the formal complaints of Kathleen Sylvester at Docket No. C‑20055455, William J. Finkler at Docket No. C-20055473, and James Pugh at Docket No. C‑20065850 are sustained.
3. That the civil penalties assessed against WP Water Company, Inc. and WP Sanitary Company, Inc. are held in abeyance until the consolidated matters at Docket Nos. I‑00070114, and A-230550F2000 are resolved.

4. That Carl Kresge pay a civil penalty of $109,500.00 by certified check or money order as provided in section 3301(a) of the Public Utility Code, 66 Pa. C.S. § 3301(a), within twenty (20) days after the final Commission Order in this proceeding to:
Pennsylvania Public Utility Commission

P.O. Box 3265

Harrisburg, PA 17105-3265
5. That Sandra Kresge pay a civil penalty of $109,500.00 by certified check or money order as provided in section 3301(a) of the Public Utility Code, 66 PA. C.S. § 3301(a), within twenty (20) days after the final Commission Order in this proceeding to:
Pennsylvania Public Utility Commission

P.O. Box 3265

Harrisburg, PA 17105-3265

6. That the civil penalties herein imposed shall not be recoverable by WP Water Company, Inc. or WP Sanitary, Inc. in any future rate proceeding.

7. That the formal complaints at Docket Nos. C-20055453, C-20055455, C‑20055473, C-20055473, C-20065849, and C-20065850 be marked closed.

Date:
August 16, 2007 



_________________________________








Ember S. Jandebeur







Administrative Law Judge
� 	Mr. Kresge testified that the Companies were acquired in 1986; however, records indicated the Companies were acquired in 1985.


� 	Mr. Pries mailed a letter to PUC Secretary McNulty withdrawing his complaint on December 8, 2005.


� 	The PUC formal complaint form has check off boxes for electric, gas water, steam heat, wastewater, motor carrier, and telephone.  Complainants Sylvester and Finkler checked off water and wastewater.  Complainant Pugh, as will be addressed later in this decision, had no complaint against WP Water.


� 	Mr. Pugh, having filed his complaint on January 9, 2006, did not receive the January 4, 2006 notice for the February 27, 2006 hearing.  The matter was not docketed until February 8, 2006.  The undersigned ALJ sent him a letter on March 23, 2006 enclosing copies of the (then current) actions.  He was allowed to join the proceeding belatedly, and testified at a later hearing.


� 	The correct Docket is No. 820308.


� 	National Pollution Discharge Elimination System


� 	§ 65.7(d) in full states:  A public utility shall provide a meter to each of its water customers except fire protection customers and shall furnish water service, except fire protection service, exclusively on a metered basis; except that flat rate service may continue to be provided pending implementation of a reasonable metering program or under special circumstances as may be permitted by the Commission for good cause.


� 	For the 52 customers’ current in 1991, the failure to comply is from March 31, 1995 the date of this Initial Decision.  For the 100 customers connected after the issuance of the Order on April 26, 1991, the number of years in violation varies with the date of their connections.  These dates were not made part of the record.


� 	SFoF refers to Stipulated Finding of Fact; FoF refers to Finding of Fact.


�	The 31st is arbitrary, as the Order did not state a specific date in March, it merely indicated to comply by March 1995.





PAGE  
i

