PENNSYLVANIA PUBLIC UTILITY COMMISSION

HARRISBURG, PENNSYLVANIA  17105-3265

	Luke Kelley 
         v. 
Pennsylvania Electric Company
	
	Public Meeting held June 21, 2007

	
	
	JUN-2007-ALJ-0140*

	
	
	

	
	
	Docket No.  C-20066673


MOTION OF CHAIRMAN WENDELL F. HOLLAND

Before us today is an Initial Decision which dismisses the complaint filed by Luke Kelley against Pennsylvania Electric Company (Penelec) for the failure to satisfy the burden of proof.
In mid-June of 2006, Mr. Kelley noticed that whenever one of his appliances requiring a lot of amperage was turned on, such as a dryer or air conditioner, the lights in his house would brighten.  Also, Mr. Kelley turned on the radio and his stereo system which began to emit smoke.  He immediately unplugged the receiver and checked the receptacle with his meter and read the voltage as between 190 and 200 volts.  According to Mr. Kelley, this indicated the existence of a “loose neutral”.  Mr. Kelley viewed the transformer in question that serves his house and three others.  Based on his observation, he believes that his was the last house to be connected and there was not sufficient room in the transformer to have his neutral completely underneath the lug.
At the hearing in this case, Penelec witness Wright testified that a trouble call was received from Mr. Kelley on July 13, 2006.  Personnel were dispatched quickly to Mr. Kelley’s service location to investigate the problem.  Mr.Wright testified that the cause of Mr. Kelley’s service problem was determined to be a bad neutral connection on the transformer pole.  Based on his years of experience and the information provided by the lineman, Mr. Wright opined that the failure of the neutral was caused by corrosion.  Penelec argues although it has performed routine maintenance on this circuit, and has repaired controls on the circuit, the bad neutral would not have been discoverable.  Such connections are not visible to the naked eye as part of the maintenance and repair inspection.  Failed neutral connections are found by line crews inspecting a circuit after a trouble call such as received from Mr. Kelley.  Penelec witness Wright testified that the neutral connection which failed on July 13, 2006 had been in place since 1986.  It is his opinion that this is a reasonable amount of time for a neutral connection to last.

The Administrative Law Judge accepted the Company’s argument that the neutral connection simply rotted off the transformer and rejected Mr. Kelly’s observation that the connection was not properly attached.  
I am troubled by the Company's testimony in this case.  According to the Company's testimony, the neutral connection had been installed approximately 20 years prior and that this was a reasonable period of time for this connection to last.  In view of the fact that the failure of this utility installed equipment could result in significant damages and losses for the consumer, I fail to understand why this equipment was not subject to periodic inspection.  I believe that it would be appropriate to remand this case to develop the record concerning the industry standards for inspection of this utility equipment.  In addition, I would like an examination of the frequency of the inspections of the specific utility equipment involved in this proceeding.

THEREFORE, I MOVE:

1.
That this case be remanded to the office of Administrative Law Judge for further development of the record.

2.
That the Office of Special Assistants prepare the appropriate Opinion and Order.
__________________________


_________________________________





DATE






WENDELL F. HOLLAND, CHAIRMAN


