Contents

Design and Construction - LNG Storage Tanks	2

Design and Construction - Fire Protection	3

Design and Construction - Security and Protective Enclosures	5

CRM, SCADA, and Leak Detection - Control Room Management	8

Emergency Preparedness and Response - Emergency Response Liquids	8

Facilities and Storage - Facilities General	11

Facilities and Storage - Tanks and Storage	19

Maintenance and Operations - Liquid Pipeline Maintenance	20

Maintenance and Operations - Liquid Pipeline Operations	26

Reporting - Regulatory Reporting (Traditional)	33

Time-Dependent Threats - External Corrosion - Atmospheric	35

Time-Dependent Threats - External Corrosion - Cathodic Protection	36

Time-Dependent Threats - Internal Corrosion - Preventive Measures	40

Time-Dependent Threats - Time Dependent Threats: General	41

Training and Qualification - Operator Qualification	41

Training and Qualification - Training of Personnel	45

NTSB Recommendations Review	46

## 2025 LNG PHMSA IA DEMO - LNG

## Design and Construction - LNG Storage Tanks

56. Cooldown of Components Does the process specify design limits for thermal stress of components during cooldown? (MO.LO.COOLDOWN.P). 193.2017 (193.2503(g); 193.2505(a); 193.2505(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

57. Cooldown of Components Do records indicate that cooldown of components was maintained within design limits? (MO.LO.COOLDOWN.R). 193.2505(a) (193.2505(b); 193.2503(g); 193.2101; 193.2301) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

58. Cooldown of Components Do field observations confirm design limits are adhered to during cooldown and leak checks were performed on components subject to cryogenic temperatures following stabilization? (MO.LO.COOLDOWN.O). 193.2505(b) (193.2301; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Design and Construction - Fire Protection

2. Fire Protection Evaluation Do records indicate that an adequate fire protection evaluation has been conducted as required by NFPA 59A, Section 9.1.2? (FS.FG.FIREPROTEVAL.R). 193.2801 (NFPA 59A, Section 9.1.2; NFPA 600; NFPA 72; NFPA 1221) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. ESD - Source Shutdown / Isolation Do records demonstrate that the emergency shutdown system meets the requirements of NFPA 59A, Section 9.2? (FS.FG.ESDSOURCE.R). 193.2801 (NFPA 59A, Section 9.2) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. ESD - Source Shutdown / Isolation Do field observations confirm the emergency shutdown system (ESD) has been installed that meets the requirements of NFPA 59A (2001), Section 9.2, for source shutoff and isolation? (FS.FG.ESDSOURCE.O). 193.2801 (NFPA 59A, Section 9.2; 193.2301; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Flammable Gas, Low Temperature and Fire Detection Do records indicate that flammable gas and fire detection systems meet the requirements of NFPA 59A (2001), Section 9.3? (FS.FG.FIREDETECT.R). 193.2801 (NFPA 59A, Section 9.3; 193.2101(a); 193.2301; 193.2101(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Flammable Gas, Low Temperature and Fire Detection Do field observations confirm that the flammable gas and fire detection systems meet the requirements of NFPA 59A (2001), Section 9.3, by location performance and alarm announcement? (FS.FG.FIREDETECT.O). 193.2801 (NFPA 59A, Section 9.3; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Fire Water Supply and Delivery Do records demonstrate that the fire water supply and distribution system meet the requirements of NFPA 59A (2001), Section 9.4? (FS.FG.FIREWATERDIST.R). 193.2801 (NFPA 59A, Section 9.4) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. Fire Water Supply and Delivery Do field observations confirm the fire water supply and delivery system meet the requirements of NFPA 59A (2001), Section 9.4? (FS.FG.FIREWATERDIST.O). 193.2801 (NFPA 59A, Section 9.4; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

16. Fire Protection Equipment Do records demonstrate the staging of fire protection equipment meets the requirements of NFPA 59A (2001), Section 9.5? (FS.FG.FIREPROTEQUIP.R). 193.2801 (NFPA 59A, Section 9.5; 193.2101(a); 193.2301; 193.2101(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

17. Fire Protection Equipment Do field observations confirm the staging of fire protection equipment meets the requirements of NFPA 59A (2001), Section 9.5? (FS.FG.FIREPROTEQUIP.O). 193.2801 (193.2303; NFPA 59A, Section 9.5) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Design and Construction - Security and Protective Enclosures

3. Enclosure Protection and Construction Do field observations verify applicable facilities are surrounded by adequate protective enclosures? (FS.FG.PROTECTENCLOSE.O). 193.2905(a) (193.2905(b); 193.2905(c); 193.2905(d); 193.2905(e); 193.2907(a); 193.2907(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Protective Enclosure Construction Do records indicate protective enclosures are constructed in accordance with 193.2907? (FS.FG.PROTECTENCLOSURECON.R). 193.2907(a) (193.2905(a); 193.2905(b); 193.2905(c); 193.2905(d); 193.2905(e); 193.2907(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Security Lighting Does the process require adequate facility security lighting be provided? (FS.FG.SECURITYLIGHT.P). 193.2911 (193.2017(a); 193.2017(b); 193.2017(c)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Security Lighting Do field observations verify adequate security lighting is provided, where applicable? (FS.FG.SECURITYLIGHT.O). 193.2911 (193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Security Monitoring Does the process for security monitoring meet requirements for the facility? (FS.FG.SECURITYMONITOR.P). 193.2913 (193.2017(a)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Security Monitoring Do field observations verify security monitoring meets the requirements applicable to the facility? (FS.FG.SECURITYMONITOR.O). 193.2913 (193.2303; 193.2905(a)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Security System Alternate Source of Power Does the process require an adequate alternate (back-up) source of power for security lighting, and security monitoring and warning systems? (FS.FG.ALTPOWER.P). 193.2915 (193.2445(a); 193.2445(b); 193.2017(a); 193.2017(b); 193.2017(c)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

15. Security System Alternate Source of Power Do field observations verify there is an alternate (back-up) power source for security lighting and security monitoring and warning systems? (FS.FG.ALTPOWER.O). 193.2915 (193.2445(a); 193.2445(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

16. Warning Signs Does the process require the placement of warning signs along the protective enclosure? (FS.FG.WARNSIGN.P). 193.2017(a) (193.2917(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

18. Warning Signs Do field observations verify warning signs are placed about the protective enclosure such that they can be seen from 100 ft at night? (FS.FG.WARNSIGN.O). 193.2917(a) (193.2907(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## CRM, SCADA, and Leak Detection - Control Room Management

1. Control Center Does the control center have the required capabilities and characteristics, and does it monitor components and buildings? (CR.CRM.CONTROLCENTER.O). 193.2441(a) (193.2441(b); 193.2441(c); 193.2441(d); 193.2441(e); 193.2507). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Emergency Preparedness and Response - Emergency Response Liquids

1. Responding to Non-Fire Emergencies Does the process identify the types and locations of non-fire emergencies that may be expected to occur? (EP.ERL.EMEROPS.P). 193.2017(a) (193.2509(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Responding to Controllable Emergencies Do emergency procedures contain provisions for responding to controllable emergencies? (EP.ERL.CONTREMERG.P). 193.2017(a) (193.2509(b)(1)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Responding to Uncontrollable Emergencies Do emergency procedures contain provisions for responding to uncontrollable emergencies? (EP.ERL.UNCONTREMERG.P). 193.2017(a) (193.2509(b)(2)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Responding to Emergencies Do records convey that operator adequately responded to emergencies and followed its emergency response procedures? (EP.ERL.EMERG.R). 193.2509(b)(1) (193.2509(b)(2)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Coordination of Evacuation Plans Do emergency procedures require a process for coordinating evacuation plans with local officials? (EP.ERL.EVACUATION.P). 193.2017(a) (193.2509(b)(3)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Coordination of Evacuation Plans Do records show that evacuation plans were coordinated with local authorities? (EP.ERL.EVACUATION.R). 193.2509(b)(3). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Cooperating on Mutual Assistance Do emergency procedures require cooperating with local officials in evacuations and emergencies requiring mutual assistance? (EP.ERL.MUTUALASSIST.P). 193.2017(a) (193.2509(b)(4)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. Cooperating on Mutual Assistance Do records show cooperation with local officials on mutual assistance? (EP.ERL.MUTUALASSIST.R). 193.2509(b)(4). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Emergency Personnel Protective Clothing and Equipment Does the process require that protective clothing and equipment be provided to personnel performing emergency response duties? (EP.ERL.EMERPERSONPROT.P). 193.2017(a) (193.2509(b)(1); 193. 2511(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Personnel Protective Clothing and Equipment Is emergency protective clothing and equipment at the locations and of the type specified? (EP.ERL.EMERPERSONPROT.O). 193.2511(a). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Protection from Thermal Radiation Does the process require that personnel on duty at fixed locations be provided protection from thermal radiation or a means of escape? (EP.ERL.THERMRADPROT.P). 193.2017(a) (193.2511(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Protection from Thermal Radiation Is a means of protection from thermal radiation or a means of escape provided at applicable fixed duty locations? (EP.ERL.THERMRADPROT.O). 193.2511(b). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. First-aid Material Availability Does the process require that first-aid material be readily available and properly marked? (EP.ERL.FIRSTAID.P). 193.2511(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. First-Aid Material Availability Is first aid material readily available and clearly marked? (EP.ERL.FIRSTAID.O). 193.2511(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Facilities and Storage - Facilities General

1. Fire Protection Evaluation Do records indicate that an adequate fire protection evaluation has been conducted as required by NFPA 59A, Section 9.1.2? (FS.FG.FIREPROTEVAL.R). 193.2801 (NFPA 59A, Section 9.1.2; NFPA 600; NFPA 72; NFPA 1221) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. ESD - Source Shutdown / Isolation Do records demonstrate that the emergency shutdown system meets the requirements of NFPA 59A, Section 9.2? (FS.FG.ESDSOURCE.R). 193.2801 (NFPA 59A, Section 9.2) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. ESD - Source Shutdown / Isolation Do field observations confirm the emergency shutdown system (ESD) has been installed that meets the requirements of NFPA 59A (2001), Section 9.2, for source shutoff and isolation? (FS.FG.ESDSOURCE.O). 193.2801 (NFPA 59A, Section 9.2; 193.2301; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Flammable Gas, Low Temperature and Fire Detection Do records indicate that flammable gas and fire detection systems meet the requirements of NFPA 59A (2001), Section 9.3? (FS.FG.FIREDETECT.R). 193.2801 (NFPA 59A, Section 9.3; 193.2101(a); 193.2301; 193.2101(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Flammable Gas, Low Temperature and Fire Detection Do field observations confirm that the flammable gas and fire detection systems meet the requirements of NFPA 59A (2001), Section 9.3, by location performance and alarm announcement? (FS.FG.FIREDETECT.O). 193.2801 (NFPA 59A, Section 9.3; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Fire Water Supply and Delivery Do records demonstrate that the fire water supply and distribution system meet the requirements of NFPA 59A (2001), Section 9.4? (FS.FG.FIREWATERDIST.R). 193.2801 (NFPA 59A, Section 9.4) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Fire Water Supply and Delivery Do field observations confirm the fire water supply and delivery system meet the requirements of NFPA 59A (2001), Section 9.4? (FS.FG.FIREWATERDIST.O). 193.2801 (NFPA 59A, Section 9.4; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. Fire Protection Equipment Do records demonstrate the staging of fire protection equipment meets the requirements of NFPA 59A (2001), Section 9.5? (FS.FG.FIREPROTEQUIP.R). 193.2801 (NFPA 59A, Section 9.5; 193.2101(a); 193.2301; 193.2101(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Fire Protection Equipment Do field observations confirm the staging of fire protection equipment meets the requirements of NFPA 59A (2001), Section 9.5? (FS.FG.FIREPROTEQUIP.O). 193.2801 (193.2303; NFPA 59A, Section 9.5) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Protective Clothing Do records demonstrate that protective clothing was available in accordance with NFPA 59A, Sections 9.7.1 and 9.7.2? (FS.FG.PROTCLOTHING.R). 193.2801 (NFPA 59A, Section 9.7). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Protective Clothing Is protective clothing available as required by NFPA 59A, Section 9.7.1 and 9.7.2? (FS.FG.PROTCLOTHING.O). 193.2801 (NFPA 59A, Section 9.7). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Entering Confined or Hazardous Space Do the written practices and procedures for the entry of personnel into confined or hazardous space meet the requirements of NFPA 59A, Section 9.7.3? (FS.FG.CONFINEDSPACE.P). 193.2017(a) (193.2801). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Entry Into Confined or Hazardous Space Are written practices and procedures adequately implemented for the entry of personnel into confined or hazardous spaces? (FS.FG.CONFINEDSPACE.O). 193.2801 (NFPA 59A, Section 9.7). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. Availability of Gas Detectors Are at least three portable gas detectors readily available at the plant in accordance with NFPA 59A, Section 9.7.4? (FS.FG.GASDETECTORS.O). 193.2801 (NFPA 59A, Sections 9.7). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

15. Venting in Case of Emergency Does the process for depressurizing the plant or venting LNG in the event of an emergency meet the requirements of NFPA 59A, Section 9.9.1? (FS.FG.VENTING.P). 193.2017(a) (193.2801; NFPA 59A, Sections 9.7). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

16. Taking an LNG Container Out of Service Does the process for taking an LNG container out of service meet the requirements of NFPA 59A, Section 9.9.2? (FS.FG.OUTOFSERVICE.P). 193.2017(a) (193.2801). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

17. Taking an LNG Container Out of Service Do records demonstrate that an LNG container taken out of service was performed in accordance with NFPA 59A, Section 9.9.2? (FS.FG.OUTOFSERVICE.R). 193.2801 (NFPA 59A, Section 9.9). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

18. Security Procedures Is the security process adequate? (FS.FG.SECPROCEDURES.P). 193.2017(a) (193.2903(a); 193.2903(b); 193.2903(c); 193.2903(d); 193.2903(e); 193.2903(f); 193.2903(g)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

19. Protective Enclosure Construction Do records indicate protective enclosures are constructed in accordance with 193.2907? (FS.FG.PROTECTENCLOSURECON.R). 193.2907(a) (193.2905(a); 193.2905(b); 193.2905(c); 193.2905(d); 193.2905(e); 193.2907(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

20. Enclosure Protection and Construction Do field observations verify applicable facilities are surrounded by adequate protective enclosures? (FS.FG.PROTECTENCLOSE.O). 193.2905(a) (193.2905(b); 193.2905(c); 193.2905(d); 193.2905(e); 193.2907(a); 193.2907(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

21. Security Communication Does the process require an effective means of security communications? (FS.FG.SECURITYCOMM.P). 193.2909(a) (193.2909(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

22. Security Communications Are there adequate security communication capabilities? (FS.FG.SECURITYCOMM.O). 193.2909(a) (193.2909(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

23. Security Lighting Does the process require adequate facility security lighting be provided? (FS.FG.SECURITYLIGHT.P). 193.2911 (193.2017(a); 193.2017(b); 193.2017(c)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

24. Security Lighting Do field observations verify adequate security lighting is provided, where applicable? (FS.FG.SECURITYLIGHT.O). 193.2911 (193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

25. Security Monitoring Does the process for security monitoring meet requirements for the facility? (FS.FG.SECURITYMONITOR.P). 193.2913 (193.2017(a)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

26. Security Monitoring Do field observations verify security monitoring meets the requirements applicable to the facility? (FS.FG.SECURITYMONITOR.O). 193.2913 (193.2303; 193.2905(a)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

27. Security System Alternate Source of Power Does the process require an adequate alternate (back-up) source of power for security lighting, and security monitoring and warning systems? (FS.FG.ALTPOWER.P). 193.2915 (193.2445(a); 193.2445(b); 193.2017(a); 193.2017(b); 193.2017(c)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

28. Security System Alternate Source of Power Do field observations verify there is an alternate (back-up) power source for security lighting and security monitoring and warning systems? (FS.FG.ALTPOWER.O). 193.2915 (193.2445(a); 193.2445(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

29. Sources of Power Does the process require at least two sources of power for communication, emergency lighting, and firefighting systems? (FS.FG.POWERSOURCES.P). 193.2445(a) (193.2445(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

30. Sources of Power Are there at least two sources of power for communication, emergency lighting, and firefighting systems? (FS.FG.POWERSOURCES.O). 193.2445(a) (193.2445(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

31. Warning Signs Does the process require the placement of warning signs along the protective enclosure? (FS.FG.WARNSIGN.P). 193.2017(a) (193.2917(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

32. Warning Signs Do field observations verify warning signs are placed about the protective enclosure such that they can be seen from 100 ft at night? (FS.FG.WARNSIGN.O). 193.2917(a) (193.2907(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Facilities and Storage - Tanks and Storage

1. LNG Storage Tanks Does the process require that LNG storage tanks be inspected or tested to verify tank safety and structural integrity? (FS.TS.LNGSTRGTANK.P). 193.2017(a) (193.2605(b); 193.2623(a); 193.2623(b); 193.2623(c); 193.2623(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. LNG Storage Tanks Do records show that LNG storage tanks have been adequately inspected? (FS.TS.LNGSTRGTANK.R). 193.2639(a) (193.2623(a); 193.2623(b); 193.2623(c); 193.2623(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. LNG Storage Tanks Do LNG storage tanks appear structurally sound and safe? (FS.TS.LNGSTRGTANK.O). 193.2623(a) (193.2623(b); 193.2623(c); 193.2623(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Maintenance and Operations - Liquid Pipeline Maintenance

1. Status of Components Does the process meet the general requirements for the condition and status of components? (MO.LM.CMPNTSTATUS.P). 193.2017(a) (193.2603(a); 193.2603(b); 193.2603(d); 193.2603(e); 193.2605(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Status of Components Do records show that the status of out of service components was documented as required? (MO.LM.CMPNTSTATUS.R). 193.2639(a) (193.2603(c); 193.2603(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Maintenance Procedures Does the operator have procedures for the maintenance of each component, including any required corrosion control? (MO.LM.MAINTPROCEDURES.P). 193.2017(a) (193.2605(a); 193.2605(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Recognizing Safety-related Conditions Does the maintenance process contain instructions for recognizing a reportable safety-related condition? (MO.LM.MAINTSRC.P). 193.2017(a) (193.2605(a); 193.2605(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Control of Foreign Material and Debris Does the process require that the facility be free from the presence of foreign material and debris? (MO.LM.FOREIGNMAT.P). 193.2017(a) (193.2607(a); 193.2607(b); 193.2605(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Control of Foreign Material and Debris Is the facility free of foreign material or debris that presents a fire hazard? (MO.LM.FOREIGNMAT.O). 193.2607(a) (193.2607(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Physical Support Systems Does the process require that foundations and support systems be inspected for changes that could impair their support? (MO.LM.PHYSICALSUPPORT.P). 193.2017(a) (193.2605(b); 193.2609). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. Physical Support Systems Do records show that foundations and support systems have been inspected? (MO.LM.PHYSICALSUPPORT.R). 193.2639(a) (193.2609). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Physical Support Systems Are foundations and support systems structurally sound? (MO.LM.PHYSICALSUPPORT.O). 193.2609. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Maintain Fire Protection Equipment Has a maintenance program been established for all plant fire protection equipment in accordance with NFPA 59A, Section 9.6? (MO.LM.MAINTAINFIREPROTEQ.P). 193.2017(a) (193.2801; NFA 59A, Section 9.6). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Maintain Fire Protection Equipment Do records demonstrate an adequate maintenance program for plant fire protection equipment in accordance with NFPA 59A Section 9.6? (MO.LM.MAINTAINFIREPROTEQ.R). 193.2801 (NFPA 59A Section 9.6). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Fire Protection Out of Service Does the process require that the amount of fire control equipment out of service at any one time be minimized? (MO.LM.FIREPROTOOS.P). 193.2017(a) (193.2611(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Fire Protection Out of Service Do records show that maintenance activities on fire protection equipment are scheduled to minimize downtime and ensure a minimum amount of equipment is available? (MO.LM.FIREPROTOOS.R). 193.2639(a) (193.2611(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. Maintain Access Routes Does the process require that access routes for movement of fire protection equipment be kept clear? (MO.LM.FIREPROTACCESS.P). 193.2017(a) (193.2605(b); 193.2611(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

15. Maintain Access Routes Are access routes for movement of fire control equipment clear of snow and other obstacles? (MO.LM.FIREPROTACCESS.O). 193.2611(b). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

16. Testing Auxiliary Power Sources Does the process require that auxiliary power sources be tested monthly for operational capability and annually for capacity? (MO.LM.AUXPOWERTEST.P). 193.2017(a) (193.2605(b); 193.2613). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

17. Testing Auxiliary Power Sources Do records show that auxiliary power systems have been tested monthly for operational capability and annually for capacity? (MO.LM.AUXPOWERTEST.R). 193.2639(a) (193.2613). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

18. Testing Auxiliary Power Sources Are monthly or annual tests performed as required by the process? (MO.LM.AUXPOWERTEST.O). 193.2613. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

19. Isolating and Purging Does the process require purging of components handling flammable liquids prior to maintenance or, if the component or maintenance activity provides an ignition source, isolation of the component? (MO.LM.ISOPURGE.P). 193.2017(a) (193.2605(b); 193.2615(a); 193.2615(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

20. Repair of Components Does the process require that repairs conform to the requirements of 193 Subpart D (Construction) and assure integrity/operational safety? (MO.LM.REPAIRS.P). 193.2017(a) (193.2605(b); 193.2617(a); 193.2617(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

21. Repair of Components Do records show that repairs of components were made in accordance with 193 Subpart D (Construction) and assured integrity/operational safety? (MO.LM.REPAIRS.R). 193.2639(a) (193.2617(a); 193.2617(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

22. Control Systems Does the process require that control systems meet the requirements of 193.2619? (MO.LM.CONTROLSYS.P). 193.2017(a) (193.2605(b); 193.2619(a); 193.2619(b); 193.2619(c); 193.2619(d); 193.2619(e)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

23. Control Systems Do records show that control systems, relief valves, and other components were inspected or tested in accordance with 193.2619? (MO.LM.CONTROLSYS.R). 193.2639(a) (193.2619(b); 193.2619(c); 193.2619(d); 193.2619(e)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

24. Control Systems Are control systems operating within design limits? (MO.LM.CONTROLSYS.O). 193.2619(a). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

25. Transfer Hoses Does the process require the testing and inspection of transfer hoses before use and annually? (MO.LM.TXHOSE.P). 193.2017(a) (193.2605(b); 193.2621(a); 193.2621(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

26. Transfer Hoses Do records show that transfer hoses have been tested once each calendar year and inspected before each use? (MO.LM.TXHOSE.R). 193.2639(a) (193.2621(a); 193.2621(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

27. Transfer Hoses Are transfer hoses inspected before each use? (MO.LM.TXHOSE.O). 193.2621(b). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

28. Maintaining Maintenance Records Are records of each inspection, test and investigation maintained in accordance with 193.2639? (MO.LM.MAINTENANCERECORDS.R). 193.2639(a). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Maintenance and Operations - Liquid Pipeline Operations

1. General Process Review and Update Requirements Are there adequate requirements for review and update of plant plans and procedures? (MO.LO.PROCESSUPDATE.P). 193.2017(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. General Process Review and Update Requirements Do records show that plans and procedures have been reviewed and updated as necessary? (MO.LO.PROCESSUPDATE.R). 193.2017(c)(2). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Monitoring Operations Does the process require the monitoring of operating components and buildings for leaks, fires, and malfunctions that could cause a hazardous condition? (MO.LO.MONITOR.P). 193.2017(a) (193.2503(a), 193.2507). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Monitoring Operations Do records show that the operator monitored operating components and buildings for leaks, fires, and malfunctions that could cause a hazardous condition? (MO.LO.MONITOR.R). 193.2507 (193.2503(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Monitoring Operations - Buildings and Components Are operating components and buildings monitored for leaks, fire, and malfunctions that could cause a hazardous condition? (MO.LO.MONITOR.O). 193.2507. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Startup and Shutdown Does the process require performance testing to demonstrate that components will operate satisfactory in service during startup and shutdown? (MO.LO.STARTUPSHUTDOWN.P). 193.2017(a) (193.2503(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Startup and Shutdown Do records show that startup and shutdown procedures, including initial testing, were followed? (MO.LO.STARTUPSHUTDOWN.R). 193.2521 (193.2503(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. Startup and Shutdown Is performance testing being conducted to demonstrate that components will operate satisfactorily in service during startup and shutdown? (MO.LO.STARTUPSHUTDOWN.O). 193.2503(b). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Abnormal Operating Conditions Does the process include provisions for recognizing abnormal operating conditions? (MO.LO.ABNORMALOPS.P). 193.2017(a) (193.2503(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Abnormal Operating Conditions Do records show personnel responded to indications of abnormal operations as required by the AOC procedures? (MO.LO.ABNORMALOPS.R). 193.2521 (193.2503(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Purging and Inerting Does the process require that components that could accumulate significant amounts of combustible mixtures be adequately purged? (MO.LO.PURGEINERT.P). 193.2017(a) (193.2503(d); 193.2517). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Purging and Inerting Do records show that components that could accumulate significant amounts of combustible mixture were adequately purged? (MO.LO.PURGEINERT.R). 193.2517 (193.2503(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Purging and Inerting Is purging of components that can accumulate significant amounts of combustible mixture conducted in accordance with procedures? (MO.LO.PURGEINERT.O). 193.2517. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. Vaporization Design Limits Does the process require that vaporizers operate within design limits? (MO.LO.VAPORIZATION.P). 193.2017(a) (193.2503(e)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

15. Vaporization Design Limits Do records show that vaporizers operated within their design limits? (MO.LO.VAPORIZATION.R). 193.2503(e). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

16. Liquefaction Design Limits Does the process require that liquefaction units operate within their design limits? (MO.LO.LIQUEFACTION.P). 193.2017(a) (193.2503(f)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

17. Liquefaction Design Limits Do records show that components operated within their liquefaction design limits? (MO.LO.LIQUEFACTION.R). 193.2503(f). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

18. Cooldown of Components Does the process specify design limits for thermal stress of components during cooldown? (MO.LO.COOLDOWN.P). 193.2017 (193.2503(g); 193.2505(a); 193.2505(b)) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

19. Cooldown of Components Do records indicate that cooldown of components was maintained within design limits? (MO.LO.COOLDOWN.R). 193.2505(a) (193.2505(b); 193.2503(g); 193.2101; 193.2301) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

20. Cooldown of Components Do field observations confirm design limits are adhered to during cooldown and leak checks were performed on components subject to cryogenic temperatures following stabilization? (MO.LO.COOLDOWN.O). 193.2505(b) (193.2301; 193.2303) Note: this question is presented in multiple places so you will see multiple instances of it on this report.. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

21. Transfer of LNG Is the process adequate for the transfer of LNG or other hazardous fluids? (MO.LO.LNGTRANS.P). 193.2017(a) (193.2513(a); 193.2513(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

22. Transfer of LNG Do records show that LNG transfers were conducted in accordance with requirements? (MO.LO.LNGTRANS.R). 193.2513(a) (193.2513(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

23. Transfer of LNG Are LNG transfers conducted in accordance with the process? (MO.LO.LNGTRANS.O). 193.2513(b). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

24. Cargo Transfer Process Does the process require the cargo transfer procedures be located at the transfer area and contain the provisions of 193.2513(c)? (MO.LO.CARGOTRANS.P). 193.2017(a) (193.2513(a); 193.2513(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

25. Cargo Transfer Process Do records show that cargo transfers were conducted in accordance with the process? (MO.LO.CARGOTRANS.R). 193.2513(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

26. Cargo Transfer Process Are cargo transfers conducted in accordance with the process? (MO.LO.CARGOTRANS.O). 193.2513(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

27. Investigation of Failures Does the process require that failures be investigated? (MO.LO.FAILINVESTIGATE.P). 193.2515(a) (193.2515(b); 193.2515(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

28. Investigation of Failures Do records show that the operator adequately investigated failures? (MO.LO.FAILINVESTIGATE.R). 193.2521 (193.2515(a); 193.2515(b); 193.2515(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

29. Communication Systems Does the process require an adequate communication system? (MO.LO.COMMSYS.P). 193.2519(a) (193.2519(b); 193.2519(c); 193.2445(a); 193.2445(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

30. Communication Systems Does the communication system meet all of the requirements of 193.2519? (MO.LO.COMMSYS.O). 193.2519(a) (193.2519(b); 193.2519(c); 193.2445(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

31. Maintaining Operating Records Is there an adequate process for maintaining the records of each inspection, test and investigation required by Part 193? (MO.LO.OPERATINGRECORD.P). 193.2017(a) (193.2521). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

32. Maintaining Operating Records Are records of each inspection, test and investigation maintained in accordance with 193.2521? (MO.LO.OPERATINGRECORDS.R). 193.2521. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Reporting - Regulatory Reporting (Traditional)

1. Immediate Reporting: Incidents Does process require incidents to be immediately reported to the National Response Center? (RPT.RR.IMMEDREPORT.P). 193.2011 (191.3; 191.5(a); 191.5(b); 191.7(a); 191.7(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Immediate Reporting: Incidents Do records indicate immediate reports of incidents were made in accordance with 193.2011? (RPT.RR.IMMEDREPORT.R). 193.2011 (191.3; 191.5(a); 191.5(b); 191.7(a); 191.7(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Incident Reports Does the process require preparation and filing of an incident report as soon as practicable but no later than 30 days after discovery of a reportable incident? (RPT.RR.INCIDENTREPORT.P). 193.2011 (191.15(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Incident Reports Do records indicate reportable incidents were identified and reports were submitted on DOT Form PHMSA 7100.3 within the required timeframe? (RPT.RR.INCIDENTREPORT.R). 193.2011 (191.15(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Supplemental Incident Reports Does the process require preparation and filing of supplemental incident reports? (RPT.RR.INCIDENTREPORTSUPP.P). 193.2011 (191.15(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Supplemental Incident Reports Do records indicate accurate supplemental incident reports were filed and within the required timeframe? (RPT.RR.INCIDENTREPORTSUPP.R). 193.2011 (191.15(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Annual Report Records Have complete and accurate Annual Reports been submitted? (RPT.RR.ANNUALREPORT.R). 193.2011 (191.17(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. NPMS: Annual Updates Do records indicate: NPMS submissions are completed each year, on or before March 15, representing all plants as of December 31 of the previous year, and if no modifications occurred an email to that effect was submitted? (RPT.RR.NPMSANNUAL.R). 191.29(a) (191.29(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. National Registry of Pipeline and LNG Operators (OPID) Does the process require the appropriate control of Operator Identification Numbers (OPIDs) and notification of applicable changes to the National Registry of Pipeline and LNG Operators? (RPT.RR.REGISTRY.P). 193.2011 (191.22(a); 191.22(b); 191.22(c); 191.22(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. National Registry of Pipeline and LNG Operators (OPID) Do records indicate appropriate control of Operator Identification Numbers (OPIDs) and the National Registry of Pipeline and LNG Operators has been notified of applicable changes, including changes in entity, acquisition/divestiture, and construction in accordance with 191.22? (RPT.RR.REGISTRY.R). 193.2011 (191.22(a); 191.22(b); 191.22(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Safety Related Condition Reports Does the process require preparation and filing of safety related condition reports? (RPT.RR.SRCR.P). 193.2011 (191.23(a); 191.23(b); 191.25(a); 191.25(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Safety Related Condition Reports Do records indicate safety-related condition reports were filed as required? (RPT.RR.SRCR.R). 193.2011 (191.23(a); 191.23(b); 191.25(a); 191.25(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Time-Dependent Threats - External Corrosion - Atmospheric

1. Atmospheric Corrosion Does the process require that components subject to atmospheric corrosive attack are made of corrosion-resistant materials or are coated/jacketed? (TD.ATM.ATMCORROSION.P). 193.2017(a) (193.2605(b); 193.2627(a); 193.2627(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Monitoring for Atmospheric Corrosion Does the process require that each component that is protected from atmospheric corrosion be inspected at intervals not to exceed 3 years? (TD.ATM.ATMCORRMONITOR.P). 193.2017(a) (193.2605(b); 193.2635(d)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Monitoring for Atmospheric Corrosion Do records show that inspections for atmospheric corrosion were completed at the required intervals? (TD.ATM.ATMCORRMONITOR.R). 193.2639(b) (193.2635(d); 193.2639(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Monitoring for Atmospheric Corrosion Are certain components subject to atmospheric corrosive attack coated or jacketed? (TD.ATM.ATMCORRMONITOR.O). 193.2635(d). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Time-Dependent Threats - External Corrosion - Cathodic Protection

1. Buried or Submerged Components Does the process require that buried components are made of a corrosion-resistant material, or protected by coating and cathodic protection? (TD.CP.BURIEDCOMP.P). 193.2017(a) (193.2605(b); 193.2629(a); 193.2629(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Buried or Submerged Components Do records show that applicable buried and submerged components are protected from external corrosion? (TD.CP.BURIEDCOMP.R). 193.2639(b) (193.2629(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Interference Currents Does the process give sufficient guidance and detail for identifying areas of potential interference currents and minimizing the detrimental effects of such currents? (TD.CP.INTFRCURRENT.P). 193.2017(a) (193.2605(b); 193.2633(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Interference Currents Do records show that the operator has a continuing program to minimize the detrimental effects of interference currents? (TD.CP.INTFRCURRENT.R). 193.2639(b) (193.2633(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Isolation of Adjacent Metal Components and Systems Does the process require that cathodic protection be installed to minimize the detrimental effects on adjacent metal components and communication and control systems? (TD.CP.ISOLATE.P). 193.2017(a) (193.2605(b); 193.2633(b); 193.2633(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Monitoring for External Corrosion Does the process require that each buried or submerged component be tested for cathodic protection adequacy at least once each calendar year not to exceed 15 months? (TD.CP.EXTCORRMONITOR.P). 193.2017(a) (193.2605(b); 193.2635(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Monitoring for External Corrosion Do records show that buried or submerged components cathodic protection adequacy was tested once each calendar year not to exceed 15 months? (TD.CP.EXTCORRMONITOR.R). 193.2639(b) (193.2635(a); 193.2639(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. Monitoring for External Corrosion For certain buried or submerged components, does the cathodic protection meet the requirements of §192.463? (TD.CP.EXTCORRMONITOR.O). 193.2635(a). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Rectifiers, Bonds, Diodes and Reverse Current Switches Does the process require making electrical checks of rectifiers or other impressed current power source, interference bonds, reverse current switches and diodes at the code specified frequencies? (TD.CP.CURRENTTEST.P). 193.2017(a) (193.2605(b); 193.2635(b); 193.2635(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Rectifiers, Bonds, Diodes and Reverse Current Switches Do records show adequate electrical checks of rectifiers or other impressed current power source, interference bonds, reverse current switches and diodes and at the required intervals? (TD.CP.CURRENTTEST.R). 193.2369(b) (193.2635(b); 193.2635(c); 193.2639(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Rectifiers, Bonds, Diodes and Reverse Current Switches Are rectifiers, interference bonds, diodes, and reverse current switches properly maintained and are they functioning properly? (TD.CP.CURRENTTEST.O). 193.2635(b) (193.2635(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Prompt Remedial Action Does the process require that prompt remedial action be taken whenever corrosion control deficiencies are found? (TD.CP.REMEDIATE.P). 193.2017(a) (193.2605(b); 193.2637). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Prompt Remedial Action Do records show that prompt corrective or remedial action was taken whenever corrosion control deficiencies were found? (TD.CP.REMEDIATE.R). 193.2639(b) (193.2637; 193.2639(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. CP Maps and Records Does the operator have records showing cathodically protected components, structures bonded to the CP system, and corrosion protection equipment? (TD.CP.RECORDS.R). 193.2639(b) (193.2639(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Time-Dependent Threats - Internal Corrosion - Preventive Measures

1. Internal Corrosion Does the process require that components subject to internal corrosive attack be made of corrosion-resistant material or be otherwise protected? (TD.ICP.INTCORR.P). 193.2017(a) (193.2605(b); 193.2631(a); 193.2631(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Monitoring for Internal Corrosion Does the process require that internal corrosion monitoring devices be checked at least twice each calendar year, not to exceed 7.5 months? (TD.ICP.INTCORRMONITOR.P). 193.2017(a) (193.2605(b); 193.2635(e)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Monitoring for Internal Corrosion Do records show that internal corrosion monitoring devices were checked twice per calendar year, not to exceed 7.5 months? (TD.ICP.INTCORRMONITOR.R). 193.2639(b) (193.2635(e); 193.2639(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Time-Dependent Threats - Time Dependent Threats: General

1. Corrosion Does the process require that components that can be adversely affected by corrosion be identified, and protected, or inspected and replaced? (TD.GEN.CORROSION.P). 193.2017(a) (193.2605(b); 193.2625(a); 193.2625(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Corrosion Do records show that components that can be adversely affected by corrosion are identified, and protected, or inspected and replaced? (TD.GEN.CORROSION.R). 193.2639(b) (193.2625(a); 193.2625(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Training and Qualification - Operator Qualification

1. Qualifications and Training of Operations and Maintenance Personnel Does the process define the qualifications and training requirements for personnel who operate and maintain components? (TQ.OQ.OMQUAL.P). 193.2707(a) (193.2707(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Qualifications and Training of Operations and Maintenance Personnel Do records show that operations and maintenance of components was conducted by personnel who met the qualifications and training requirements? (TQ.OQ.OMQUAL.R). 193.2719(a) (193.2707(a); 193.2707(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Qualifications and Training of Operations and Maintenance Personnel Do individuals conducting operations and maintenance of components demonstrate their capability to perform their assigned functions? (TQ.OQ.OMQUAL.O). 193.2707(a) (193.2707(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Qualifications and Training of Corrosion Control Personnel Does the process require that corrosion control of cathodic protection systems be carried out by, or under the direction of, personnel qualified by training or experience in corrosion control technology? (TQ.OQ.CORRCONTRPERS.P). 193.2707(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Qualifications and Training of Corrosion Control Personnel Do records demonstrate that personnel who perform corrosion control, or supervise unqualified individuals, are qualified in corrosion control technology? (TQ.OQ.CORRCONTRPERS.R). 193.2719(a) (193.2707(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

6. Qualifications and Training of Corrosion Control Personnel Do individuals conducting, or directing, corrosion control activities demonstrate adequate skills and knowledge? (TQ.OQ.CORRCONTRPERS.O). 193.2707(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

7. Personnel Health Is there an adequate plan for evaluating the health and physical condition of personnel assigned operations, maintenance, security, or fire protection duties? (TQ.OQ.PERSONHEALTH.P). 193.2017(a) (193.2711). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

8. Personnel Health Do records show that the health and physical condition of personnel assigned operations, maintenance, security, or fire protection duties have been evaluated? (TQ.OQ.PERSONHEALTH.R). 193.2711. Sat+; Sat; Concern; Unsat; NA; NC. Notes.

9. Training of Operations, Maintenance, and Supervisory Personnel Does the plan require that operations, maintenance, and supervisory personnel receive the mandatory initial training? (TQ.OQ.TRAINOM.P). 193.2017(a) (193.2713(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

10. Training of Operations, Maintenance, and Supervisory Personnel Do records show that operations, maintenance, and supervisory personnel have received the mandatory initial training? (TQ.OQ.TRAINOM.R). 193.2713(a) (193.2719(a); 193.2719(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

11. Retraining of Operations, Maintenance, and Supervisory Personnel Does the plan require that operations, maintenance, and supervisory personnel receive refresher training at intervals not to exceed two years? (TQ.OQ.RETRAINOM.P). 193.2017(a) (193.2713(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

12. Retraining of Operations, Maintenance, and Supervisory Personnel Do records show that operations, maintenance, and supervisory personnel received refresher training every two years? (TQ.OQ.RETRAINOM.R). 193.2713(b) (193.2719(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

13. Training of Security Personnel Does the plan require that security personnel receive the mandatory initial training? (TQ.OQ.TRAINSECURITY.P). 193.2017(a) (193.2715(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

14. Training of Security Personnel Do records show that security personnel received mandatory initial training? (TQ.OQ.TRAINSECURITY.R). 193.2715(a) (193.2719(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

15. Retraining of Security Personnel Does the plan require that security personnel receive refresher training at intervals not to exceed two years? (TQ.OQ.RETRAINSECURITY.P). 193.2017(a) (193.2715(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

16. Retraining of Security Personnel Do records show that security personnel received refresher training every two years? (TQ.OQ.RETRAINSECURITY.R). 193.2715(b) (193.2719(a)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## Training and Qualification - Training of Personnel

1. Training Fire Protection Personnel Does the plan require that operations, maintenance, and supervisory personnel receive initial fire protection training that meets the requirements of 193.2717(a)? (TQ.TR.TRAINFIREPROT.P). 193.2017(a) (193.2717(a); 193.2717(c); 193.2801). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. Training Personnel in Fire Protection Do records show that operations, maintenance, and supervisory personnel have been adequately trained in fire protection, including plant fire drills? (TQ.TR.TRAINFIREPROT.R). 193.2717(a) (193.2717(a)(1); 193.2717(a)(2); 193.2717(a)(3); 193.2717(c); 193.2719(a); 193.2719(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

3. Retraining of Personnel in Fire Protection Does the plan require that operations, maintenance, and supervisory personnel receive refresher fire protection training at intervals not to exceed two years and that training includes fire drills? (TQ.TR.RETRAINFIREPROT.P). 193.2017(a) (193.2717(b); 193.2717(c)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

4. Retraining of Personnel in Fire Protection Do records show that operations, maintenance, and supervisory personnel received refresher fire protection training every two years, including plant fire drills? (TQ.TR.RETRAINFIREPROT.R). 193.2717(b) (193.2717(c); 193.2719(a); 193.2719(b)). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

5. Plant Fire Drills Do personnel demonstrate adequate fire protection skills during a fire drill? (TQ.TR.FIREDRILLS.O). 193.2717(c). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

## NTSB Recommendations Review

1. NTSB Recommendations Review Does the operator have procedures in place for reviewing NTSB Recommendations? (GENERIC.NTSB.NTSBREVIEW.P). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

2. NTSB Recommendations Review Do the records verify operator conducted reviews of NTSB recommendations and implemented appropriate actions? (GENERIC.NTSB.NTSBREVIEW.R). Sat+; Sat; Concern; Unsat; NA; NC. Notes.

Except as required to be disclosed by law, any inspection documentation, including completed protocol forms, summary reports, executive summary reports, and enforcement documentation are for internal use only by federal or state pipeline safety regulators. Some inspection documentation may contain information which the operator considers to be confidential. In addition, supplemental inspection guidance and related documents in the file library are also for internal use only by federal or state pipeline safety regulators (with the exception of documents published in the federal register, such as advisory bulletins). Do not distribute or otherwise disclose such material outside of the state or federal pipeline regulatory organizations. Requests for such information from other government organizations (including, but not limited to, NTSB, GAO, IG, or Congressional Staff) should be referred to PHMSA Headquarters Management.