Contents

[Field Review - Field Review 3](#_Toc157931657)

[Procedures - Reporting 11](#_Toc157931658)

[Procedures - Plans and Procedures 12](#_Toc157931659)

[Procedures - Normal Operations 13](#_Toc157931660)

[Procedures - Emergency Operations 14](#_Toc157931661)

[Procedures - Personnel Safety 16](#_Toc157931662)

[Procedures - Transfer 16](#_Toc157931663)

[Procedures - Investigation of Failure 17](#_Toc157931664)

[Procedures - Communication System 17](#_Toc157931665)

[Procedures - Operating Record 18](#_Toc157931666)

[Procedures - Maintenance 18](#_Toc157931667)

[Procedures - Support System 19](#_Toc157931668)

[Procedures - Fire Protection Procedures 19](#_Toc157931669)

[Procedures - Auxiliary Power Source 20](#_Toc157931670)

[Procedures - Isolating and Purging 21](#_Toc157931671)

[Procedures - Repair 21](#_Toc157931672)

[Procedures - Control System 21](#_Toc157931673)

[Procedures - Testing Transfer Hose 22](#_Toc157931674)

[Procedures - Inspecting LNG Storage Tank 22](#_Toc157931675)

[Procedures - Corrosion Protection 22](#_Toc157931676)

[Procedures - Atmospheric Corrosion 23](#_Toc157931677)

[Procedures - External Corrosion Control: Buried or Submerged Components 23](#_Toc157931678)

[Procedures - Internal Corrosion Control 23](#_Toc157931679)

[Procedures - Interference Currents 24](#_Toc157931680)

[Procedures - Monitoring Corrosion Control 24](#_Toc157931681)

[Procedures - Remedial Measure 25](#_Toc157931682)

[Procedures - Operations and Maintenance 26](#_Toc157931683)

[Procedures - Personnel Health 26](#_Toc157931684)

[Procedures - Training: Operations and Maintenance 27](#_Toc157931685)

[Procedures - Training: Security 27](#_Toc157931686)

[Procedures - Training: Fire Protection 28](#_Toc157931687)

[Procedures - Fire Protection 28](#_Toc157931688)

[Procedures - Security 29](#_Toc157931689)

[Procedures - Security Communications 29](#_Toc157931690)

[Procedures - Security Lightning 30](#_Toc157931691)

[Procedures - Security Monitoring 30](#_Toc157931692)

[Procedures - Alternative Power Source 30](#_Toc157931693)

[Procedures - Warning Sign 31](#_Toc157931694)

[Records - Regulatory Reporting Performance 31](#_Toc157931695)

[Records - Operating 33](#_Toc157931696)

[Records - Maintenance 36](#_Toc157931697)

[Records - Maintenance: Transfer Hoses 38](#_Toc157931698)

[Records - Maintenance: Storage Tank 38](#_Toc157931699)

[Records - Maintenance: Corrosion Control 39](#_Toc157931700)

[Records - Personnel Health 41](#_Toc157931701)

[Records - Initial and Follow-up Training 41](#_Toc157931702)

[Records - Fire Protection 43](#_Toc157931703)

[Records - Protective Enclosures 45](#_Toc157931704)

## UGI LNG – LNG

## Field Review - Field Review

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Control Center Does the control center have the required capabilities and characteristics, and does it monitor components and buildings? (CR.CRM.CONTROLCENTER.O)  |
| 193.2441(a) (193.2441(b); 193.2441(c); 193.2441(d); 193.2441(e); 193.2507)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Sources of Power Are there at least two sources of power for communication, emergency lighting, and firefighting systems? (FS.FG.POWERSOURCES.O)  |
| 193.2445(a) (193.2445(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Startup and Shutdown Is performance testing being conducted to demonstrate that components will operate satisfactorily in service during startup and shutdown? (MO.LO.STARTUPSHUTDOWN.O)  |
| 193.2503(b)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Cooldown of Components Do field observations confirm leak checks were performed on components subject to cryogenic temperatures following stabilization? (MO.LO.COOLDOWN.O)  |
| 193.2505(b) (193.2301; 193.2303)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Monitoring Operations - Buildings and Components Are operating components and buildings monitored for leaks, fire, and malfunctions that could cause a hazardous condition? (MO.LO.MONITOR.O)  |
| 193.2507  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Personnel Protective Clothing and Equipment Is emergency protective clothing and equipment at the locations and of the type specified? (EP.ERL.EMERPERSONPROT.O)  |
| 193.2511(a)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Protection from Thermal Radiation Is a means of protection from thermal radiation or a means of escape provided at applicable fixed duty locations? (EP.ERL.THERMRADPROT.O)  |
| 193.2511(b)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 8. First-Aid Material Availability Is first aid material readily available and clearly marked? (EP.ERL.FIRSTAID.O)  |
| 193.2511(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 9. Transfer of LNG Are LNG transfers conducted in accordance with the process? (MO.LO.LNGTRANS.O)  |
| 193.2513(b)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 10. Cargo Transfer Process Are cargo transfers conducted in accordance with the process? (MO.LO.CARGOTRANS.O)  |
| 193.2513(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 11. Purging and Inerting Is purging of components that can accumulate significant amounts of combustible mixture conducted in accordance with procedures? (MO.LO.PURGEINERT.O)  |
| 193.2517  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 12. Communication Systems Does the communication system meet all of the requirements of 193.2519? (MO.LO.COMMSYS.O)  |
| 193.2519(a) (193.2519(b); 193.2519(c); 193.2445(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 13. Control of Foreign Material and Debris Is the facility free of foreign material or debris that presents a fire hazard? (MO.LM.FOREIGNMAT.O)  |
| 193.2607(a) (193.2607(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 14. Physical Support Systems Are foundations and support systems structurally sound? (MO.LM.PHYSICALSUPPORT.O)  |
| 193.2609  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 15. Maintain Access Routes Are access routes for movement of fire control equipment clear of snow and other obstacles? (MO.LM.FIREPROTACCESS.O)  |
| 193.2611(b)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 16. Testing Auxiliary Power Sources Are monthly or annual tests performed as required by the process? (MO.LM.AUXPOWERTEST.O)  |
| 193.2613  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 17. Control Systems Are control systems operating within design limits? (MO.LM.CONTROLSYS.O)  |
| 193.2619(a)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 18. Transfer Hoses Are transfer hoses inspected before each use? (MO.LM.TXHOSE.O)  |
| 193.2621(b)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 19. LNG Storage Tanks Do LNG storage tanks appear structurally sound and safe? (FS.TS.LNGSTRGTANK.O)  |
| 193.2623(a) (193.2623(b); 193.2623(c); 193.2623(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 20. Monitoring for External Corrosion For certain buried or submerged components, does the cathodic protection meet the requirements of §192.463? (TD.CP.EXTCORRMONITOR.O)  |
| 193.2635(a)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 21. Rectifiers, Bonds, Diodes and Reverse Current Switches Are rectifiers, interference bonds, diodes, and reverse current switches properly maintained and are they functioning properly? (TD.CP.CURRENTTEST.O)  |
| 193.2635(b) (193.2635(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 22. Monitoring for Atmospheric Corrosion Are certain components subject to atmospheric corrosive attack coated or jacketed? (TD.ATM.ATMCORRMONITOR.O)  |
| 193.2635(d)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 23. Qualifications and Training of Operations and Maintenance Personnel Do individuals conducting operations and maintenance of components demonstrate their capability to perform their assigned functions? (TQ.OQ.OMQUAL.O)  |
| 193.2707(a) (193.2707(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 24. Qualifications and Training of Corrosion Control Personnel Do individuals conducting, or directing, corrosion control activities demonstrate adequate skills and knowledge? (TQ.OQ.CORRCONTRPERS.O)  |
| 193.2707(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 25. Plant Fire Drills Do personnel demonstrate adequate fire protection skills during a fire drill? (TQ.TR.FIREDRILLS.O)  |
| 193.2717(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 26. ESD - Source Shutdown / Isolation Do field observations confirm the emergency shutdown system (ESD) has been installed that meets the requirements of NFPA 59A (2001), Section 9.2, for source shutoff and isolation? (FS.FG.ESDSOURCE.O)  |
| 193.2801 (NFPA 59A, Section 9.2; 193.2301; 193.2303)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 27. Flammable Gas, Low Temperature and Fire Detection Do field observations confirm that the flammable gas and fire detection systems meet the requirements of NFPA 59A (2001), Section 9.3, by location performance and alarm announcement? (FS.FG.FIREDETECT.O)  |
| 193.2801 (NFPA 59A, Section 9.3; 193.2303)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 28. Fire Water Supply and Delivery Do field observations confirm the fire water supply and delivery system meet the requirements of NFPA 59A (2001), Section 9.4? (FS.FG.FIREWATERDIST.O)  |
| 193.2801 (NFPA 59A, Section 9.4; 193.2303)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 29. Fire Protection Equipment Do field observations confirm the staging of fire protection equipment meets the requirements of NFPA 59A (2001), Section 9.5? (FS.FG.FIREPROTEQUIP.O)  |
| 193.2801 (193.2303; NFPA 59A, Section 9.5)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 30. Protective Clothing Is protective clothing available as required by NFPA 59A, Section 9.7.1 and 9.7.2? (FS.FG.PROTCLOTHING.O)  |
| 193.2801 (NFPA 59A, Section 9.7)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 31. Entry Into Confined or Hazardous Space Are written practices and procedures adequately implemented for the entry of personnel into confined or hazardous spaces? (FS.FG.CONFINEDSPACE.O)  |
| 193.2801 (NFPA 59A, Section 9.7)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 32. Availability of Gas Detectors Are at least three portable gas detectors readily available at the plant in accordance with NFPA 59A, Section 9.7.4? (FS.FG.GASDETECTORS.O)  |
| 193.2801 (NFPA 59A, Sections 9.7)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 33. Enclosure Protection and Construction Do field observations verify applicable facilities are surrounded by adequate protective enclosures? (FS.FG.PROTECTENCLOSE.O)  |
| 193.2905(a) (193.2905(b); 193.2905(c); 193.2905(d); 193.2905(e); 193.2907(a); 193.2907(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 34. Security Communications Are there adequate security communication capabilities? (FS.FG.SECURITYCOMM.O)  |
| 193.2909(a) (193.2909(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 35. Security Lighting Do field observations verify adequate security lighting is provided, where applicable? (FS.FG.SECURITYLIGHT.O)  |
| 193.2911 (193.2303)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 36. Security Monitoring Do field observations verify security monitoring meets the requirements applicable to the facility? (FS.FG.SECURITYMONITOR.O)  |
| 193.2913 (193.2303; 193.2905(a); )  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 37. Security System Alternate Source of Power Do field observations verify there is an alternate (back-up) power source for security lighting and security monitoring and warning systems? (FS.FG.ALTPOWER.O)  |
| 193.2915 (193.2445(a); 193.2445(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 38. Warning Signs Do field observations verify warning signs are placed about the protective enclosure such that they can be seen from 100 ft at night? (FS.FG.WARNSIGN.O)  |
| 193.2917(a) (193.2907(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Reporting

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Immediate Reporting: Incidents Does process require incidents to be immediately reported to the National Response Center? (RPT.RR.IMMEDREPORT.P)  |
| 193.2011 (191.3; 191.5(a); 191.5(b); 191.7(a); 191.7(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Incident Reports Does the process require preparation and filing of an incident report as soon as practicable but no later than 30 days after discovery of a reportable incident? (RPT.RR.INCIDENTREPORT.P)  |
| 193.2011 (191.15(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Supplemental Incident Reports Does the process require preparation and filing of supplemental incident reports? (RPT.RR.INCIDENTREPORTSUPP.P)  |
| 193.2011 (191.15(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. National Registry of Pipeline and LNG Operators (OPID) Does the process require the appropriate control of Operator Identification Numbers (OPIDs) and notification of applicable changes to the National Registry of Pipeline and LNG Operators? (RPT.RR.REGISTRY.P)  |
| 193.2011 (191.22(a); 191.22(b); 191.22(c); 191.22(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Safety Related Condition Reports Does the process require preparation and filing of safety related condition reports? (RPT.RR.SRCR.P)  |
| 193.2011 (191.23(a); 191.23(b); 191.25(a); 191.25(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Plans and Procedures

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. General Process Review and Update Requirements Are there adequate requirements for review and update of plant plans and procedures? (MO.LO.PROCESSUPDATE.P)  |
| 193.2017(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Normal Operations

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Monitoring Operations Does the process require the monitoring of operating components and buildings for leaks, fires, and malfunctions that could cause a hazardous condition? (MO.LO.MONITOR.P)  |
| 193.2017(a) (193.2503(a), 193.2507)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Startup and Shutdown Does the process require performance testing to demonstrate that components will operate satisfactory in service during startup and shutdown? (MO.LO.STARTUPSHUTDOWN.P)  |
| 193.2017(a) (193.2503(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Abnormal Operating Conditions Does the process include provisions for recognizing abnormal operating conditions? (MO.LO.ABNORMALOPS.P)  |
| 193.2017(a) (193.2503(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Purging and Inerting Does the process require that components that could accumulate significant amounts of combustible mixtures be adequately purged? (MO.LO.PURGEINERT.P)  |
| 193.2017(a) (193.2503(d); 193.2517)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Vaporization Design Limits Does the process require that vaporizers operate within design limits? (MO.LO.VAPORIZATION.P)  |
| 193.2017(a) (193.2503(e))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Liquefaction Design Limits Does the process require that liquefaction units operate within their design limits? (MO.LO.LIQUEFACTION.P)  |
| 193.2017(a) (193.2503(f))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Cooldown of Components Does the process require that the thermal stress of components be kept within design limits during cooldown? (MO.LO.COOLDOWN.P)  |
| 193.2017 (193.2503(g); 193.2505(a); 193.2505(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Emergency Operations

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Responding to Non-Fire Emergencies Does the process identify the types and locations of non-fire emergencies that may be expected to occur? (EP.ERL.EMEROPS.P)  |
| 193.2017(a) (193.2509(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Responding to Controllable Emergencies Do emergency procedures contain provisions for responding to controllable emergencies? (EP.ERL.CONTREMERG.P)  |
| 193.2017(a) (193.2509(b)(1))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Responding to Uncontrollable Emergencies Do emergency procedures contain provisions for responding to uncontrollable emergencies? (EP.ERL.UNCONTREMERG.P)  |
| 193.2017(a) (193.2509(b)(2))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Coordination of Evacuation Plans Do emergency procedures require a process for coordinating evacuation plans with local officials? (EP.ERL.EVACUATION.P)  |
| 193.2017(a) (193.2509(b)(3))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Cooperating on Mutual Assistance Do emergency procedures require cooperating with local officials in evacuations and emergencies requiring mutual assistance? (EP.ERL.MUTUALASSIST.P)  |
| 193.2017(a) (193.2509(b)(4))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Personnel Safety

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Emergency Personnel Protective Clothing and Equipment Does the process require that protective clothing and equipment be provided to personnel performing emergency response duties? (EP.ERL.EMERPERSONPROT.P)  |
| 193.2017(a) (193.2509(b)(1); 193. 2511(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Protection from Thermal Radiation Does the process require that personnel on duty at fixed locations be provided protection from thermal radiation or a means of escape? (EP.ERL.THERMRADPROT.P)  |
| 193.2017(a) (193.2511(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. First-aid Material Availability Does the process require that first-aid material be readily available and properly marked? (EP.ERL.FIRSTAID.P)  |
| 193.2511(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Transfer

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Transfer of LNG Is the process adequate for the transfer of LNG or other hazardous fluids? (MO.LO.LNGTRANS.P)  |
| 193.2017(a) (193.2513(a); 193.2513(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Cargo Transfer Process Does the process require the cargo transfer procedures be located at the transfer area and contain the provisions of 193.2513(c)? (MO.LO.CARGOTRANS.P)  |
| 193.2017(a) (193.2513(a); 193.2513(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Investigation of Failure

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Investigation of Failures Does the process require that failures be investigated? (MO.LO.FAILINVESTIGATE.P)  |
| 193.2515(a) (193.2515(b); 193.2515(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Communication System

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Communication Systems Does the process require an adequate communication system? (MO.LO.COMMSYS.P)  |
| 193.2519(a) (193.2519(b); 193.2519(c); 193.2445(a); 193.2445(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Operating Record

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Maintaining Operating Records Is there an adequate process for maintaining the records of each inspection, test and investigation required by Part 193? (MO.LO.OPERATINGRECORD.P)  |
| 193.2017(a) (193.2521)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Maintenance

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Status of Components Does the process meet the general requirements for the condition and status of components? (MO.LM.CMPNTSTATUS.P)  |
| 193.2017(a) (193.2603(a); 193.2603(b); 193.2603(d); 193.2603(e); 193.2605(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Maintenance Procedures Does the operator have procedures for the maintenance of each component, including any required corrosion control? (MO.LM.MAINTPROCEDURES.P)  |
| 193.2017(a) (193.2605(a); 193.2605(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Recognizing Safety-related Conditions Does the maintenance process contain instructions for recognizing a reportable safety-related condition? (MO.LM.MAINTSRC.P)  |
| 193.2017(a) (193.2605(a); 193.2605(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Control of Foreign Material and Debris Does the process require that the facility be free from the presence of foreign material and debris? (MO.LM.FOREIGNMAT.P)  |
| 193.2017(a) (193.2607(a); 193.2607(b); 193.2605(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Support System

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Physical Support Systems Does the process require that foundations and support systems be inspected for changes that could impair their support? (MO.LM.PHYSICALSUPPORT.P)  |
| 193.2017(a) (193.2605(b); 193.2609)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Fire Protection Procedures

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Maintain Fire Protection Equipment Has a maintenance program been established for all plant fire protection equipment in accordance with NFPA 59A, Section 9.6? (MO.LM.MAINTAINFIREPROTEQ.P)  |
| 193.2017(a) (193.2801; NFA 59A, Section 9.6)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Fire Protection Out of Service Does the process require that the amount of fire control equipment out of service at any one time be minimized? (MO.LM.FIREPROTOOS.P)  |
| 193.2017(a) (193.2611(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Maintain Access Routes Does the process require that access routes for movement of fire protection equipment be kept clear? (MO.LM.FIREPROTACCESS.P)  |
| 193.2017(a) (193.2605(b); 193.2611(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Auxiliary Power Source

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Sources of Power Does the process require at least two sources of power for communication, emergency lighting, and firefighting systems? (FS.FG.POWERSOURCES.P)  |
| 193.2445(a) (193.2445(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Testing Auxiliary Power Sources Does the process require that auxiliary power sources be tested monthly for operational capability and annually for capacity? (MO.LM.AUXPOWERTEST.P)  |
| 193.2017(a) (193.2605(b); 193.2613)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Isolating and Purging

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Isolating and Purging Does the process require purging of components handling flammable liquids prior to maintenance or, if the component or maintenance activity provides an ignition source, isolation of the component? (MO.LM.ISOPURGE.P)  |
| 193.2017(a) (193.2605(b); 193.2615(a); 193.2615(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Repair

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Repair of Components Does the process require that repairs conform to the requirements of 193 Subpart D (Construction) and assure integrity/operational safety? (MO.LM.REPAIRS.P)  |
| 193.2017(a) (193.2605(b); 193.2617(a); 193.2617(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Control System

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Control Systems Does the process require that control systems meet the requirements of 193.2619? (MO.LM.CONTROLSYS.P)  |
| 193.2017(a) (193.2605(b); 193.2619(a); 193.2619(b); 193.2619(c); 193.2619(d); 193.2619(e))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Testing Transfer Hose

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Transfer Hoses Does the process require the testing and inspection of transfer hoses before use and annually? (MO.LM.TXHOSE.P)  |
| 193.2017(a) (193.2605(b); 193.2621(a); 193.2621(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Inspecting LNG Storage Tank

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. LNG Storage Tanks Does the process require that LNG storage tanks be inspected or tested to verify tank safety and structural integrity? (FS.TS.LNGSTRGTANK.P)  |
| 193.2017(a) (193.2605(b); 193.2623(a); 193.2623(b); 193.2623(c); 193.2623(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Corrosion Protection

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Corrosion Does the process require that components that can be adversely affected by corrosion be identified, and protected, or inspected and replaced? (TD.GEN.CORROSION.P)  |
| 193.2017(a) (193.2605(b); 193.2625(a); 193.2625(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Atmospheric Corrosion

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Atmospheric Corrosion Does the process require that components subject to atmospheric corrosive attack are made of corrosion-resistant materials or are coated/jacketed? (TD.ATM.ATMCORROSION.P)  |
| 193.2017(a) (193.2605(b); 193.2627(a); 193.2627(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - External Corrosion Control: Buried or Submerged Components

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Buried or Submerged Components Does the process require that buried components are made of a corrosion-resistant material, or protected by coating and cathodic protection? (TD.CP.BURIEDCOMP.P)  |
| 193.2017(a) (193.2605(b); 193.2629(a); 193.2629(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Internal Corrosion Control

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Internal Corrosion Does the process require that components subject to internal corrosive attack be made of corrosion-resistant material or be otherwise protected? (TD.ICP.INTCORR.P)  |
| 193.2017(a) (193.2605(b); 193.2631(a); 193.2631(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Interference Currents

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Interference Currents Does the process give sufficient guidance and detail for identifying areas of potential interference currents and minimizing the detrimental effects of such currents? (TD.CP.INTFRCURRENT.P)  |
| 193.2017(a) (193.2605(b); 193.2633(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Isolation of Adjacent Metal Components and Systems Does the process require that cathodic protection be installed to minimize the detrimental effects on adjacent metal components and communication and control systems? (TD.CP.ISOLATE.P)  |
| 193.2017(a) (193.2605(b); 193.2633(b); 193.2633(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Monitoring Corrosion Control

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Monitoring for External Corrosion Does the process require that each buried or submerged component be tested for cathodic protection adequacy at least once each calendar year not to exceed 15 months? (TD.CP.EXTCORRMONITOR.P)  |
| 193.2017(a) (193.2605(b); 193.2635(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Rectifiers, Bonds, Diodes and Reverse Current Switches Does the process require making electrical checks of rectifiers or other impressed current power source, interference bonds, reverse current switches and diodes at the code specified frequencies? (TD.CP.CURRENTTEST.P)  |
| 193.2017(a) (193.2605(b); 193.2635(b); 193.2635(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Monitoring for Atmospheric Corrosion Does the process require that each component that is protected from atmospheric corrosion be inspected at intervals not to exceed 3 years? (TD.ATM.ATMCORRMONITOR.P)  |
| 193.2017(a) (193.2605(b); 193.2635(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Monitoring for Internal Corrosion Does the process require that internal corrosion monitoring devices be checked at least twice each calendar year, not to exceed 7.5 months? (TD.ICP.INTCORRMONITOR.P)  |
| 193.2017(a) (193.2605(b); 193.2635(e))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Remedial Measure

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Prompt Remedial Action Does the process require that prompt remedial action be taken whenever corrosion control deficiencies are found? (TD.CP.REMEDIATE.P)  |
| 193.2017(a) (193.2605(b); 193.2637)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Operations and Maintenance

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Qualifications and Training of Operations and Maintenance Personnel Does the process define the qualifications and training requirements for personnel who operate and maintain components? (TQ.OQ.OMQUAL.P)  |
| 193.2707(a) (193.2707(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Qualifications and Training of Corrosion Control Personnel Does the process require that corrosion control of cathodic protection systems be carried out by, or under the direction of, personnel qualified by training or experience in corrosion control technology? (TQ.OQ.CORRCONTRPERS.P)  |
| 193.2707(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Personnel Health

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Personnel Health Is there an adequate plan for evaluating the health and physical condition of personnel assigned operations, maintenance, security, or fire protection duties? (TQ.OQ.PERSONHEALTH.P)  |
| 193.2017(a) (193.2711)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Training: Operations and Maintenance

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Training of Operations, Maintenance, and Supervisory Personnel Does the plan require that operations, maintenance, and supervisory personnel receive the mandatory initial training? (TQ.OQ.TRAINOM.P)  |
| 193.2017(a) (193.2713(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Retraining of Operations, Maintenance, and Supervisory Personnel Does the plan require that operations, maintenance, and supervisory personnel receive refresher training at intervals not to exceed two years? (TQ.OQ.RETRAINOM.P)  |
| 193.2017(a) (193.2713(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Training: Security

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Training of Security Personnel Does the plan require that security personnel receive the mandatory initial training? (TQ.OQ.TRAINSECURITY.P)  |
| 193.2017(a) (193.2715(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Retraining of Security Personnel Does the plan require that security personnel receive refresher training at intervals not to exceed two years? (TQ.OQ.RETRAINSECURITY.P)  |
| 193.2017(a) (193.2715(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Training: Fire Protection

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Training Fire Protection Personnel Does the plan require that operations, maintenance, and supervisory personnel receive initial fire protection training that meets the requirements of 193.2717(a)? (TQ.TR.TRAINFIREPROT.P)  |
| 193.2017(a) (193.2717(a); 193.2717(c); 193.2801)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Retraining of Personnel in Fire Protection Does the plan require that operations, maintenance, and supervisory personnel receive refresher fire protection training at intervals not to exceed two years and that training includes fire drills? (TQ.TR.RETRAINFIREPROT.P)  |
| 193.2017(a) (193.2717(b); 193.2717(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Fire Protection

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Entering Confined or Hazardous Space Do the written practices and procedures for the entry of personnel into confined or hazardous space meet the requirements of NFPA 59A, Section 9.7.3? (FS.FG.CONFINEDSPACE.P)  |
| 193.2017(a) (193.2801)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Venting in Case of Emergency Does the process for depressurizing the plant or venting LNG in the event of an emergency meet the requirements of NFPA 59A, Section 9.9.1? (FS.FG.VENTING.P)  |
| 193.2017(a) (193.2801; NFPA 59A, Sections 9.7)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Taking an LNG Container Out of Service Does the process for taking an LNG container out of service meet the requirements of NFPA 59A, Section 9.9.2? (FS.FG.OUTOFSERVICE.P)  |
| 193.2017(a) (193.2801)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Security

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Security Procedures Is the security process adequate? (FS.FG.SECPROCEDURES.P)  |
| 193.2017(a) (193.2903(a); 193.2903(b); 193.2903(c); 193.2903(d); 193.2903(e); 193.2903(f); 193.2903(g))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Security Communications

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Security Communication Does the process require an effective means of security communications? (FS.FG.SECURITYCOMM.P)  |
| 193.2909(a) (193.2909(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Security Lightning

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Security Lighting Does the process require adequate facility security lighting be provided? (FS.FG.SECURITYLIGHT.P)  |
| 193.2911 (193.2017(a); 193.2017(b); 193.2017(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Security Monitoring

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Security Monitoring Does the process for security monitoring meet requirements for the facility? (FS.FG.SECURITYMONITOR.P)  |
| 193.2913 (193.2017(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Alternative Power Source

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Security System Alternate Source of Power Does the process require an adequate alternate (back-up) source of power for security lighting, and security monitoring and warning systems? (FS.FG.ALTPOWER.P)  |
| 193.2915 (193.2445(a); 193.2445(b); 193.2017(a); 193.2017(b); 193.2017(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Procedures - Warning Sign

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Warning Signs Does the process require the placement of warning signs along the protective enclosure? (FS.FG.WARNSIGN.P)  |
| 193.2017(a) (193.2917(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Regulatory Reporting Performance

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Immediate Reporting: Incidents Do records indicate immediate reports of incidents were made in accordance with 193.2011? (RPT.RR.IMMEDREPORT.R)  |
| 193.2011 (191.3; 191.5(a); 191.5(b); 191.7(a); 191.7(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Incident Reports Do records indicate reportable incidents were identified and reports were submitted on DOT Form PHMSA 7100.3 within the required timeframe? (RPT.RR.INCIDENTREPORT.R)  |
| 193.2011 (191.15(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Supplemental Incident Reports Do records indicate accurate supplemental incident reports were filed and within the required timeframe? (RPT.RR.INCIDENTREPORTSUPP.R)  |
| 193.2011 (191.15(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Annual Report Records Have complete and accurate Annual Reports been submitted? (RPT.RR.ANNUALREPORT.R)  |
| 193.2011 (191.17(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. NPMS: Annual Updates Do records indicate: NPMS submissions are completed each year, on or before March 15, representing all plants as of December 31 of the previous year, and if no modifications occurred an email to that effect was submitted? (RPT.RR.NPMSANNUAL.R)  |
| 191.29(a) (191.29(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. National Registry of Pipeline and LNG Operators (OPID) Do records indicate appropriate control of Operator Identification Numbers (OPIDs) and the National Registry of Pipeline and LNG Operators has been notified of applicable changes, including changes in entity, acquisition/divestiture, and construction in accordance with 191.22? (RPT.RR.REGISTRY.R)  |
| 193.2011 (191.22(a); 191.22(b); 191.22(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Safety Related Condition Reports Do records indicate safety-related condition reports were filed as required? (RPT.RR.SRCR.R)  |
| 193.2011 (191.23(a); 191.23(b); 191.25(a); 191.25(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Operating

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. General Process Review and Update Requirements Do records show that plans and procedures have been reviewed and updated as necessary? (MO.LO.PROCESSUPDATE.R)  |
| 193.2017(c)(2)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Abnormal Operating Conditions Do records show personnel responded to indications of abnormal operations as required by the AOC procedures? (MO.LO.ABNORMALOPS.R)  |
| 193.2521 (193.2503(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Vaporization Design Limits Do records show that vaporizers operated within their design limits? (MO.LO.VAPORIZATION.R)  |
| 193.2503(e)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Liquefaction Design Limits Do records show that components operated within their liquefaction design limits? (MO.LO.LIQUEFACTION.R)  |
| 193.2503(f)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Cooldown of Components Do records indicate that cooldown of components was maintained within design limits? (MO.LO.COOLDOWN.R)  |
| 193.2505(a) (193.2505(b); 193.2503(g); 193.2101; 193.2301)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Monitoring Operations Do records show that the operator monitored operating components and buildings for leaks, fires, and malfunctions that could cause a hazardous condition? (MO.LO.MONITOR.R)  |
| 193.2507 (193.2503(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Responding to Emergencies Do records convey that operator adequately responded to emergencies and followed its emergency response procedures? (EP.ERL.EMERG.R)  |
| 193.2509(b)(1) (193.2509(b)(2))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 8. Coordination of Evacuation Plans Do records show that evacuation plans were coordinated with local authorities? (EP.ERL.EVACUATION.R)  |
| 193.2509(b)(3)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 9. Cooperating on Mutual Assistance Do records show cooperation with local officials on mutual assistance? (EP.ERL.MUTUALASSIST.R)  |
| 193.2509(b)(4)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 10. Transfer of LNG Do records show that LNG transfers were conducted in accordance with requirements? (MO.LO.LNGTRANS.R)  |
| 193.2513(a) (193.2513(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 11. Cargo Transfer Process Do records show that cargo transfers were conducted in accordance with the process? (MO.LO.CARGOTRANS.R)  |
| 193.2513(c)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 12. Investigation of Failures Do records show that the operator adequately investigated failures? (MO.LO.FAILINVESTIGATE.R)  |
| 193.2521 (193.2515(a); 193.2515(b); 193.2515(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 13. Purging and Inerting Do records show that components that could accumulate significant amounts of combustible mixture were adequately purged? (MO.LO.PURGEINERT.R)  |
| 193.2517 (193.2503(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 14. Maintaining Operating Records Are records of each inspection, test and investigation maintained in accordance with 193.2521? (MO.LO.OPERATINGRECORDS.R)  |
| 193.2521  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 15. Startup and Shutdown Do records show that startup and shutdown procedures, including initial testing, were followed? (MO.LO.STARTUPSHUTDOWN.R)  |
| 193.2521 (193.2503(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Maintenance

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Status of Components Do records show that the status of out of service components was documented as required? (MO.LM.CMPNTSTATUS.R)  |
| 193.2639(a) (193.2603(c); 193.2603(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Physical Support Systems Do records show that foundations and support systems have been inspected? (MO.LM.PHYSICALSUPPORT.R)  |
| 193.2639(a) (193.2609)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Maintain Fire Protection Equipment Do records demonstrate an adequate maintenance program for plant fire protection equipment in accordance with NFPA 59A Section 9.6? (MO.LM.MAINTAINFIREPROTEQ.R)  |
| 193.2801 (NFPA 59A Section 9.6)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Fire Protection Out of Service Do records show that maintenance activities on fire protection equipment are scheduled to minimize downtime and ensure a minimum amount of equipment is available? (MO.LM.FIREPROTOOS.R)  |
| 193.2639(a) (193.2611(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Testing Auxiliary Power Sources Do records show that auxiliary power systems have been tested monthly for operational capability and annually for capacity? (MO.LM.AUXPOWERTEST.R)  |
| 193.2639(a) (193.2613)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Repair of Components Do records show that repairs of components were made in accordance with 193 Subpart D (Construction) and assured integrity/operational safety? (MO.LM.REPAIRS.R)  |
| 193.2639(a) (193.2617(a); 193.2617(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Control Systems Do records show that control systems, relief valves, and other components were inspected or tested in accordance with 193.2619? (MO.LM.CONTROLSYS.R)  |
| 193.2639(a) (193.2619(b); 193.2619(c); 193.2619(d); 193.2619(e))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 8. Maintaining Maintenance Records Are records of each inspection, test and investigation maintained in accordance with 193.2639? (MO.LM.MAINTENANCERECORDS.R)  |
| 193.2639(a)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Maintenance: Transfer Hoses

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Transfer Hoses Do records show that transfer hoses have been tested once each calendar year and inspected before each use? (MO.LM.TXHOSE.R)  |
| 193.2639(a) (193.2621(a); 193.2621(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Maintenance: Storage Tank

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. LNG Storage Tanks Do records show that LNG storage tanks have been adequately inspected? (FS.TS.LNGSTRGTANK.R)  |
| 193.2639(a) (193.2623(a); 193.2623(b); 193.2623(c); 193.2623(d))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Maintenance: Corrosion Control

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Corrosion Do records show that components that can be adversely affected by corrosion are identified, and protected, or inspected and replaced? (TD.GEN.CORROSION.R)  |
| 193.2639(b) (193.2625(a); 193.2625(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Buried or Submerged Components Do records show that applicable buried and submerged components are protected from external corrosion? (TD.CP.BURIEDCOMP.R)  |
| 193.2639(b) (193.2629(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Interference Currents Do records show that the operator has a continuing program to minimize the detrimental effects of interference currents? (TD.CP.INTFRCURRENT.R)  |
| 193.2639(b) (193.2633(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Monitoring for External Corrosion Do records show that buried or submerged components cathodic protection adequacy was tested once each calendar year not to exceed 15 months? (TD.CP.EXTCORRMONITOR.R)  |
| 193.2639(b) (193.2635(a); 193.2639(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Rectifiers, Bonds, Diodes and Reverse Current Switches Do records show adequate electrical checks of rectifiers or other impressed current power source, interference bonds, reverse current switches and diodes and at the required intervals? (TD.CP.CURRENTTEST.R)  |
| 193.2369(b) (193.2635(b); 193.2635(c); 193.2639(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Monitoring for Atmospheric Corrosion Do records show that inspections for atmospheric corrosion were completed at the required intervals? (TD.ATM.ATMCORRMONITOR.R)  |
| 193.2639(b) (193.2635(d); 193.2639(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Monitoring for Internal Corrosion Do records show that internal corrosion monitoring devices were checked twice per calendar year, not to exceed 7.5 months? (TD.ICP.INTCORRMONITOR.R)  |
| 193.2639(b) (193.2635(e); 193.2639(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 8. Prompt Remedial Action Do records show that prompt corrective or remedial action was taken whenever corrosion control deficiencies were found? (TD.CP.REMEDIATE.R)  |
| 193.2639(b) (193.2637; 193.2639(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 9. CP Maps and Records Does the operator have records showing cathodically protected components, structures bonded to the CP system, and corrosion protection equipment? (TD.CP.RECORDS.R)  |
| 193.2639(b) (193.2639(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Personnel Health

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Personnel Health Do records show that the health and physical condition of personnel assigned operations, maintenance, security, or fire protection duties have been evaluated? (TQ.OQ.PERSONHEALTH.R)  |
| 193.2711  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Initial and Follow-up Training

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Qualifications and Training of Operations and Maintenance Personnel Do records show that operations and maintenance of components was conducted by personnel who met the qualifications and training requirements? (TQ.OQ.OMQUAL.R)  |
| 193.2719(a) (193.2707(a); 193.2707(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. Qualifications and Training of Corrosion Control Personnel Do records demonstrate that personnel who perform corrosion control, or supervise unqualified individuals, are qualified in corrosion control technology? (TQ.OQ.CORRCONTRPERS.R)  |
| 193.2719(a) (193.2707(c))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Training of Operations, Maintenance, and Supervisory Personnel Do records show that operations, maintenance, and supervisory personnel have received the mandatory initial training? (TQ.OQ.TRAINOM.R)  |
| 193.2713(a) (193.2719(a); 193.2719(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Retraining of Operations, Maintenance, and Supervisory Personnel Do records show that operations, maintenance, and supervisory personnel received refresher training every two years? (TQ.OQ.RETRAINOM.R)  |
| 193.2713(b) (193.2719(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Training of Security Personnel Do records show that security personnel received mandatory initial training? (TQ.OQ.TRAINSECURITY.R)  |
| 193.2715(a) (193.2719(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Retraining of Security Personnel Do records show that security personnel received refresher training every two years? (TQ.OQ.RETRAINSECURITY.R)  |
| 193.2715(b) (193.2719(a))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Training Personnel in Fire Protection Do records show that operations, maintenance, and supervisory personnel have been adequately trained in fire protection, including plant fire drills? (TQ.TR.TRAINFIREPROT.R)  |
| 193.2717(a) (193.2717(a)(1); 193.2717(a)(2); 193.2717(a)(3); 193.2717(c); 193.2719(a); 193.2719(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 8. Retraining of Personnel in Fire Protection Do records show that operations, maintenance, and supervisory personnel received refresher fire protection training every two years, including plant fire drills? (TQ.TR.RETRAINFIREPROT.R)  |
| 193.2717(b) (193.2717(c); 193.2719(a); 193.2719(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Fire Protection

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Fire Protection Evaluation Do records indicate that an adequate fire protection evaluation has been conducted as required by NFPA 59A, Section 9.1.2? (FS.FG.FIREPROTEVAL.R)  |
| 193.2801 (NFPA 59A, Section 9.1.2; NFPA 600; NFPA 72; NFPA 1221)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 2. ESD - Source Shutdown / Isolation Do records demonstrate that the emergency shutdown system meets the requirements of NFPA 59A, Section 9.2? (FS.FG.ESDSOURCE.R)  |
| 193.2801 (NFPA 59A, Section 9.2)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 3. Flammable Gas, Low Temperature and Fire Detection Do records indicate that flammable gas and fire detection systems meet the requirements of NFPA 59A (2001), Section 9.3? (FS.FG.FIREDETECT.R)  |
| 193.2801 (NFPA 59A, Section 9.3; 193.2101(a); 193.2301; 193.2101(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 4. Fire Water Supply and Delivery Do records demonstrate that the fire water supply and distribution system meet the requirements of NFPA 59A (2001), Section 9.4? (FS.FG.FIREWATERDIST.R)  |
| 193.2801 (NFPA 59A, Section 9.4)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 5. Fire Protection Equipment Do records demonstrate the staging of fire protection equipment meets the requirements of NFPA 59A (2001), Section 9.5? (FS.FG.FIREPROTEQUIP.R)  |
| 193.2801 (NFPA 59A, Section 9.5; 193.2101(a); 193.2301; 193.2101(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 6. Protective Clothing Do records demonstrate that protective clothing was available in accordance with NFPA 59A, Sections 9.7.1 and 9.7.2? (FS.FG.PROTCLOTHING.R)  |
| 193.2801 (NFPA 59A, Section 9.7)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 7. Taking an LNG Container Out of Service Do records demonstrate that an LNG container taken out of service was performed in accordance with NFPA 59A, Section 9.9.2? (FS.FG.OUTOFSERVICE.R)  |
| 193.2801 (NFPA 59A, Section 9.9)  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

## Records - Protective Enclosures

|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|

|  |
| --- |
| 1. Protective Enclosure Construction Do records indicate protective enclosures are constructed in accordance with 193.2907? (FS.FG.PROTECTENCLOSURECON.R)  |
| 193.2907(a) (193.2905(a); 193.2905(b); 193.2905(c); 193.2905(d); 193.2905(e); 193.2907(b))  |
|   |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |
| Sat+ | Sat | Concern | Unsat | NA | NC |  |  |
|  |  |  |  |  |  |   |
| Notes |

  |

Except as required to be disclosed by law, any inspection documentation, including completed protocol forms, summary reports, executive summary reports, and enforcement documentation are for internal use only by federal or state pipeline safety regulators. Some inspection documentation may contain information which the operator considers to be confidential. In addition, supplemental inspection guidance and related documents in the file library are also for internal use only by federal or state pipeline safety regulators (with the exception of documents published in the federal register, such as advisory bulletins). Do not distribute or otherwise disclose such material outside of the state or federal pipeline regulatory organizations. Requests for such information from other government organizations (including, but not limited to, NTSB, GAO, IG, or Congressional Staff) should be referred to PHMSA Headquarters Management.