	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held December 18, 2008

	Commissioners Present:
	


	James H. Cawley, Chairman      
	

	Tyrone J. Christy, Vice Chairman   
	

	Robert F. Powelson
	

	Kim Pizzingrilli
	

	Wayne E. Gardner
	


	Letter of Notification of Duquesne Light Company filed pursuant to 52 Pa. Code Chapter 57.72 for the Construction of a 0.52 Mile Long Segment of Double Circuit 138 kV Transmission Line in Moon Township and Sewickley Borough,

Allegheny County, PA.
	Docket Number:

A-2008-2071156


ORDER

BY THE COMMISSION:

On October 24, 2008, Duquesne Light Company (“Duquesne Light”) filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(l)(iv), of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the  right-of-way.

(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the   right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present           levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.
(v) An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

 (vi)
An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with

Section 57.72(d) (3) and 57.74 (b) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Moon Township, Moon Township Municipal Authority, Allegheny County Council, Moon Township Board of Supervisors, Sewickley Borough, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.


Duquesne Light seeks Commission’s approval to construct a double-circuit 138 kV transmission line segment (“the Line”) which will connect to one circuit of its double circuit 138 kV transmission line (Brunot Island-Crescent Z-43 and Montour​Crescent Z-24) located in Moon Township.  The proposed Line will connect to and loop the Brunot Island-Crescent Z-43 circuit (Z-43) into the existing Duquesne Light Sewickley Substation located in Sewickley Borough, Pennsylvania.  The Sewickley Substation will be upgraded to accommodate this line connection.  One side of this line will be identified as Brunot Island-Sewickley Z-43 and the other side will be identified as Crescent-Sewickley Z-l43. 



The Line consists of approximately 2750 feet of new conductor from the connection point at Tower 71 on circuit Z-43 in Moon Township to the termination structure across the Ohio River in Sewickley Substation.  Approximately 1550 feet of the line is within Moon Township and 1200 feet of the line is within Sewickley Borough; both of the municipalities are located in Allegheny County.


Duquesne Light states that the Line will consist of three (3) sets of double pole structures, or a total of six (6), individual self-supporting steel poles.  One pair of these poles is located in Moon Township at the connection point to Z-43.  These poles serve as one side of the Ohio River crossing and are 85 ft. and 95 ft. in height.  The remaining four (4) poles are located in Sewickley Borough.  Two (2) of these poles located at the river crossing are 195 ft. in height.  The remaining two (2) poles are 70 ft. in height located on Duquesne Light property at Sewickley Substation.


Duquesne Light states that each circuit of the Line will consist of 3 phase conductors and one shield wire.  Each phase conductor will be 795 kcmil 20/7 Trapezoidal Aluminum Conductor Steel Supported (“ACSS/TW”) conductor and the shield wire will be a 7#8 Alumoweld conductor. 


Duquesne Light states that the proposed project is necessary to reduce overload conditions, eliminate reliability issues caused obsolete equipment and balance power flows along the transmission paths thereby improving reliability in the northeastern portion of Duquesne Light’s territory.

Duquesne Light states that the project will be designed, constructed, operated and maintained in a manner that meets or exceeds National Electrical Safety Code (“NESC”) standards and all standards of the Federal Occupational Safety and Health Administration. 

Duquesne Light states that the estimated cost of the project is $2.5 million.  The project is scheduled to start immediately following Commission approval to meet the in-service date of April 2009.
The formal Duquesne Light Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,
IT IS ORDERED:




That the Letter of Notification filed by Duquesne Light Company regarding the Construction of a 0.52 Mile Long Segment of Double Circuit 138 kV Transmission Line in Moon Township and Sewickley Borough, Allegheny County, PA., Pennsylvania, is hereby approved.

BY THE COMMISSION,

James J. McNulty

Secretary
(SEAL)

ORDER ADOPTED:  December 18, 2008,
ORDER ENTERED:  December 19, 2008
PAGE  
4

