	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17105-3265
	

	
	
	

	
	Public Meeting held April 30, 2009

	Commissioners Present:
	

	
	

	James H. Cawley, Chairman         
	

	Tyrone J. Christy, Vice Chairman 
	

	Robert F. Powelson
	

	Kim Pizzingrilli 
	

	Wayne E. Gardner
	

	
	

	Letter of Notification of Duquesne Light Company filed pursuant to 52 Pa. Code Chapter 57.72 for combining a portion of the existing Circuit 66148 and a portion of the existing Circuit Z-82 transmission lines to create a new 138 kV Circuit in Rochester Township, New Sewickley Township, Economy Borough, and Harmony Township, Beaver County, PA.
	Docket Number:

A-2009-2085800



	
	


ORDER

BY THE COMMISSION:
On January 14, 2009, Duquesne Light Company (Duquesne Light) filed a Letter of Notification pursuant to 52 Pa. Code § 57.72(d)(l)(iv) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the  right-of-way.

(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the   right-of-way.

(iv) An HV line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.
(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way. 
(vi) An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Economy Borough, Harmony Township, Rochester Township, New Sewickley Township, Beaver County Board of Commissioners, Harmony Township Board of Commission, Planning Commissions of Harmony, New Sewickley and Rochester Townships, Beaver Fall Municipal Authority and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.

Duquesne Light seeks the Commission’s approval to create a new 14.5-mile 138 kV transmission line, by combining segments of two existing lines.  A voltage increase from 69 kV to 138 kV is proposed for a 2.5-mile segment between Legionville Substation and Tower 4425 of the circuit presently identified as Ambridge-​Koppel Steel Circuit (Ckt.) 66148.  The 12-mile segment will consist of the west phases of the Crescent-Valley Ckt. Z-82 transmission line, which is currently occupied by one phase of Ckt. Z-82 and two idle conductors.  Following the proposed voltage upgrade to the Ambridge-Koppel Steel Ckt. 66148, conversion of the idled west side conductors and establishment of Ckt. Z-82 to the east side of the double circuit tower line, the new line will be identified as Valley-Legionville Ckt. Z-84.
The Crescent-Valley Ckt. Z-82 originates in Crescent Substation and terminates in the Valley Substation.  Upon completion of the proposed line, Z-82 will occupy the east side conductors and Z-84 will occupy the west side conductors from Valley Substation to Tower 206. 

Duquesne Light states that the Ambridge-Koppel Steel Ckt. 66148 currently connects the Ambridge Substation to the Koppel Steel Substation via the Legionville Substation.  Although rated for 138kV, Ckt. 66148 has continued operation at 69kV.  A voltage upgrade will be necessary for the proposed reconfiguration from Legionville Substation to Tower 4425.  Upon completion of the proposed line reconfiguration, Ckt. Z-26 will occupy the south side conductors, Ckt. Z-84 will occupy the north side conductors from Legionville Substation to Tower 4425 and the remaining portions of Ckt. 66148 will either be abandoned or used in other line reconfigurations.
Duquesne Light states that new construction consisting of one (1) steel pole near the intersection of the two existing line segments will be required.  The pole replaces Tower 205 on Ckt. Z-82.  New conductor will be necessary from Tower 206 to the new pole structure and from Tower 4425 to the new pole structure to complete the merger.  The new construction will take place entirely on Duquesne Light rights-of-way.
The Ckt. Z-82 portion of the line is located in Rochester, New Sewickley, and Economy Townships.  Approximately 15,000 feet of Ckt. Z-82 is within Rochester Township and approximately 15,000 feet of the line is within New Sewickley Township.  The remaining approximate 34,000 feet of the line portion is in Economy Township.  The Ckt. 66148 portion of the line is located in Harmony and Economy Townships.  Approximately 8,600 feet of Ckt. 66148 is within Harmony Township and approximately 5,000 feet in Economy Township.  All of the municipalities are located in Beaver County.  Approximately 92% of the lines are located on centerline rights-of-way, which have an undefined width, 7% is located on existing 85-feet right-of-way and 1% is located on Duquesne Light property.

Duquesne Light states that this project is needed because the current configuration of Legionville Substation has two (2) 138kV supply lines entering the substation.  One of these lines originates at Phillips Substation and the other line from the 69kV system via transformation to 138kV at Hopewell Substation.  Reliance on a 138/69kV autotransformer to supply 138 kV to Legionville in the event of a contingency to Legionville’s primary 138 kV supply does not conform to present day planning and design criteria.
In addition, elimination of Phillips Substation, originally constructed to support the retired Phillips Power Station, and associated conversion of the 69kV system in the area to 138kV requires upgrades at Hopewell, Koppel Steel, and Legionville Substations.  These transmission upgrades are part of Duquesne Light’s overall strategy to eliminate 69kV as a transmission supply voltage.  This strategy was created to address system inefficiencies, age of facilities, and lack of replacement parts.  Increasing the transmission supply from 69kV to 138kV increases the capacity of the transmission system, decreases the number of transformations to 69kV and consequently reduces losses and investment in 69kV autotransformers, while addressing the need for extensive rehabilitation of aging substations.  As a result, Duquesne Light’s customers benefit through increased reliability in the area.
Duquesne Light also states that presently, Ckt 66148 crosses under Ckt.    Z-82 and then again crosses over it.  Crossing of transmission lines increases the number of planned line outages since both lines are usually removed from service in order to perform maintenance on the higher circuit.  Modification of area transmission facilities from 69kV to 138kV supply has provided Duquesne Light with the opportunity to eliminate these crossovers.  The merger of these two circuits as the new Ckt. Z-84 will support the relocation of distribution facilities from older limited capacity substation locations to an existing, modern, Duquesne Light station, namely Legionville Substation.
Finally, the elimination of Ambridge Substation and the addition of another supply to Legionville Substation will use existing facilities to eliminate low voltages in the area and consolidate transmission infrastructure, thus reducing maintenance and chances of failure.

Duquesne Light states that the project will be designed, constructed, operated and maintained in a manner that meets or exceeds National Electrical Safety Code standards and all standards of the Federal Occupational Safety and Health Administration. 
Duquesne Light also states that the estimated cost of the project is $100,000.  The project is scheduled to start following Commission’s approval and will be completed by May 2009.
The formal Duquesne Light Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,
IT IS ORDERED:

That the Letter of Notification filed by Duquesne Light Company regarding the combining of a portion of the existing Circuit 66148 and a portion of the existing Circuit Z-82 transmission lines to create a new 138 kV Circuit in Rochester Township, New Sewickley Township, Economy Borough, and Harmony Township, Beaver County, PA, is hereby approved.

[image: image1.emf]
BY THE COMMISSION,

James J. McNulty

Secretary

(SEAL)

ORDER ADOPTED:  April 30, 2009
ORDER ENTERED:  April 30, 2009
PAGE  
6

