# BEFORE THE

PENNSYLVANIA PUBLIC UTILITY COMMISSION

William McLafferty					:

:

v.						:		C-2009-2101144

:

Duquesne Light Company				:

# INITIAL DECISION

Before

John H. Corbett, Jr.

Administrative Law Judge

# HISTORY OF THE PROCEEDING

This decision denies a complaint that William McLafferty (“Complainant”) filed on April 2, 2009.  Mr. McLafferty challenges the lawfulness and justness of Duquesne Light Company (“Respondent” or “Duquesne Light”) upgrading its existing transmission facilities in a right-of way across his property in a manner that exceeds the easement granted to it.  In addition, he alleges Duquesne Light began this project without giving the public an opportunity to comment and without informing the affected property owners of the inherent dangers posed by high-power lines.  Further, he avers Duquesne Light threatens to remove certain trees on his property without just compensation.  For relief, he asks that the Commission direct Respondent to undertake a number of remedial safety measures relating to operation of its high-power lines, to save his trees and to compensate him for any property damage.  Duquesne Light answered the complaint on May 8, 2009.

I received this case assignment on June 23, 2009.  On the same day, a standard Prehearing Order was issued.

A hearing was held on August 3, 2009.  Complainant appeared pro se and submitted one exhibit.  Krysia Kubiak, Esq. represented Respondent, which offered eight exhibits for admission into the record.  The hearing generated 148 pages of notes of testimony.  The record closed on September 2, 2009.

FINDINGS OF FACT

- Complainant, William McLafferty, resides with his wife and son at 121 Earlwood Road, Pittsburgh, Pennsylvania 15235, where he has lived since December 31, 1984 (N.T. 6-7).

- Respondent, Duquesne Light Company, runs a 69 kV transmission line over a right-of-way on the McLafferty property (N.T. 8-9).

- Duquesne Light was granted an easement to run a transmission line over this property in 1927 (N.T. 9, 22-28; Complainant’s Exh. 1).

- The 69 kV transmission line was in place on Complainant’s property when the house was built in 1945 (N.T. 34).

- In September 2008, Mr. McLafferty received notice that Duquesne Light was proposing to replace its existing 69 kV transmission line and towers with a 138 kV transmission line and facilities in his community, but he claims he never received notice of a public hearing where he could be heard on the subject (N.T. 7-8, 139).

- Duquesne Light has commenced construction on this project, but has not yet reached Complainant’s property (N.T. 8, 33).

- Mr. McLafferty has a number of concerns relating to the safe operation of Duquesne Light’s transmission facilities (N.T. 10).

- During a snowy night in December 1991, a portion of the 69 kV transmission line came down on Complainant’s house roof and trees that Duquesne Light now wants to remove as part of this project.  The Penn Hills Police and Volunteer Fire Departments responded immediately; Duquesne Light personnel arrived later.  With assistance from firefighters, Complainant and his family exited the rear of their house and sought shelter with a neighbor (N.T. 10-11, 15, 35-38).

- In May 1998, a portion of the transmission line fell onto Complainant’s roof and trees that Duquesne Light now wishes to remove.  The downed line caught a tree on fire in a neighbor’s yard across the road.  Mr. McLafferty called the Penn Hills Police Department, which dispatched fire units to the scene (N.T. 11-12, 15, 35-38).

- In May 1998, Mr. McLafferty was a police lieutenant in charge of the Emergency Services Division of the Penn Hills Police Department.  His responsibilities included search and rescue and the supervision of around 30 civilian paramedics in addition to regular police duties.  Following a career in police work, Mr. McLafferty retired from the Penn Hills Police Department in April 2001.  Currently, he is a fraud investigator in the Office of Inspector General for the Commonwealth of Pennsylvania (N.T. 12, 21-22).

- In June 2000, a portion of the transmission line fell onto Complainant’s property.  His wife located a Duquesne Light crew working some distance away and demanded that they return with her to attend to the problem at her location.  The crew member, who responded, could not remove the line nor cut the power (N.T. 12-13, 15, 35-38).

- Mr. McLafferty does not know what caused the transmission line to come down in any of the three incidents (N.T. 15).

- Mr. McLafferty believes the trees that Duquesne Light now wishes to remove saved his wife and family from personal injury and his home from destruction during these power line incidents (N.T. 13, 16, 20, 28-29, 139).

- Mr. McLafferty wants the Commission to direct Duquesne Light to preserve his trees (N.T. 28).

- Several years ago, Complainant claims Duquesne Light personnel damaged a dog pen that has not been properly repaired (N.T. 32-33).

- Mr. McLafferty is afraid that Duquesne Light has not provided for the safety of anyone in lawful proximity to this transmission line.  He asserts Duquesne Light depends upon fire, police and emergency medical personnel to respond to emergencies involving its transmission line facilities, but Duquesne Light has not trained them on how to deal with these situations (N.T. 13-14, 17-18, 29, 140).

- Mr. McLafferty avers Duquesne Light possesses inadequate personnel to respond appropriately to incidents involving downed power lines (N.T. 16, 28-29, 139-40).

- Mr. McLafferty wants the Commission to require Duquesne Light to have sufficient personnel on duty, who are trained and equipped to respond to these emergencies (N.T. 29-30).

- Mr. McLafferty contends that Duquesne Light blindly re-energizes a line without knowing whether a person is in contact with the line or whether the line is in contact with an occupied structure (N.T. 16).

- Mr. McLafferty wants Duquesne Light to provide assurance that he and his family will not be electrocuted by high-power lines falling on their house (N.T. 30, 140-41).

- On September 19, 2008, Duquesne Light sent to local public officials and affected property owners a letter informing them of the proposed transmission line upgrade project and inviting them to two informal public workshops on September 29-30, 2008.  It provided information relating to right-of-way, transmission line location, vegetation management construction, engineering, public safety, energy efficiency, and a need for the line (N.T. 34-35, 91-93; Respondent’s Exh. 1).

- Mr. McLafferty attended both workshops (N.T. 35).

- As part of its vegetation maintenance practice, Duquesne Light selectively removes any trees under its transmission lines that have the potential to reach the conductors (N.T. 44, 61).

- Duquesne Light wants to remove five trees that are underneath its transmission line on Complainant’s property, i.e., a pin oak, a spruce, two sugar maples, and a basswood (N.T. 44-53, 120-21; Respondent’s Exh. 2).

- These trees may grow anywhere from 70 to 100 feet tall and have the potential to contact the transmission line conductors, which will be 70-80 feet above ground; some species are capable of growing to 120 feet in height (N.T. 54, 56, 120-21, 127).

- A 4 kV distribution circuit also runs in front of Complainant’s property along Earlwood Road (N.T. 47-48; Respondent’s Exh. 2).

- Duquesne Light has cut or trimmed all of the trees in the right-of-way along the route of the transmission line, except for these trees on Complainant’s property (N.T. 53).

- Mr. McLafferty agreed to allow Duquesne Light to remove all of these trees except the pin oak, which is situated in front of his house along Earlwood Road (N.T. 53, 57-58; Respondent’s Exh. 2).

- Duquesne Light considers the pin oak to be a very prolific grower, capable of interfering with its transmission line (N.T. 49-50, 120-21; Respondent’s Exh. 2).

- Duquesne Light has computerized business records covering the last 11 years for outages that occurred on its system; it maintains hardcopy records of these events for seven years (N.T. 62-63).

- On May 19, 1998 during a storm, the 69 kV transmission line on Complainant’s property fell into the 4 kV distribution circuit on Earlwood Road, which also fell, causing an outage (N.T. 63-65, 136; Respondent’s Exhs. 3 & 8).

- When a transmission line falls into a distribution line, automatic protective equipment will attempt to isolate the problem; then automatic reclosure equipment in the field and the substation will attempt to re-energize the line in an attempt to restore service.  This operation will occur automatically two or three times before the line is finally de-energized.  This practice follows Duquesne Light’s experience that 80% of all faults are temporary.  Since all of its lines are bare copper/aluminum and western Pennsylvania is heavily treed, giving the breakers a chance to de-energize and then reclose will oftentimes restore service automatically after car accidents or when tree branches contact the lines in wind storms (N.T. 65-67).

- Duquesne Light has about 100 69 kV, 138 kV and 345 kV transmission lines covering approximately 600 miles in its service territory (N.T. 67).

- In the last 11 years, Duquesne Light had five instances where transmission line conductors came down (N.T. 67).

- Duquesne Light has no record of downed transmission lines in 1991 (N.T. 67).

- Duquesne Light has no record of downed transmission lines in 2000 or 2001 (N.T. 67).

- Duquesne Light is unaware of any catastrophic personal injury or property damage resulting from downed transmission lines in the last 28 years (N.T. 62, 68, 79).

- Duquesne Light linemen are trained to handle a downed and energized 4 kV distribution line, but cannot handle a downed and energized 69 kV transmission line.  The 69 kV transmission line would have to be de-energized first (N.T. 68, 87).

- To de-energize the 69 kV Colfax-Highland transmission line crossing the McLafferty property, a Duquesne Light operator would have to go to the Colfax substation, open the switch and lock it open, then perform the same function at the Highland substation at the other end of the line (N.T. 68-69).

- After the 69 kV transmission line is de-energized, it is then safe for the linemen to work on (N.T. 69).

- On May 19, 1998 at 8:14 p.m., a tree fell into the 69 kV Colfax-Highland transmission line, which fell into the 4 kV distribution circuit running along Earlwood Road, during a storm causing a power outage (N.T. 70-71, 77-79; Respondent’s Exh. 3).

- During this event, a reclosure on nearby Saltsburg Road on the 4 kV distribution circuit opened and closed automatically several times in order to isolate the fault and re-energize the line before it stayed open and locked out; service was restored at 3:30 a.m. (N.T. 71, 77-79; Respondent’s Exh. 3).

- Duquesne Light has no record of re-energizing the 69 kV transmission line before the fault condition was cleared (N.T. 83).

- Duquesne Light sets a reclosure on its system to operate as a circuit breaker to sense when too much power attempts to cross a line.  If the power exceeds the threshold, the reclosure will automatically open de-energizing the line.  The reclosure will then attempt to re-energize the line two or three times with a delay of 10 seconds between each event before it finally stays open (N.T. 71-72, 86).

- A reclosure on a 69 kV transmission line would operate automatically once in an attempt to re-energize the line before finally staying open (N.T. 75, 97).

- Duquesne Light cut out the reclosures on this 69 kV transmission line in 1976, so they could not have reclosed and re-energized the line.  Once the breakers operated in 1/10 of a second, the 69 kV transmission line would have remained locked out and de-energized (N.T. 98-100).

- As part of the upgrade for this line, Duquesne Light will be installing new gas microprocessor relay breakers, which will operate in about 0.075 seconds (N.T. 100).

- Duquesne Light hypothesizes that the only way for the 69 kV transmission line to become re-energized after the breakers locked out on May 19, 1998 was by contact with the live 4 kV distribution line, until it also became locked out (N.T. 98-99).

- Duquesne Light’s highest priority is to public safety and to respond to a report of a line down (N.T. 73).

- Duquesne Light’s response time to a report of a line down will depend upon the number of calls it receives during a given time (N.T. 73).

- During a storm, Duquesne Light may receive as many as 100 calls within 10 minutes reporting lines down (N.T. 73, 84).

- Duquesne Light personnel may take anywhere from 10 minutes to one-half hour to respond to a report of a downed line depending upon the number of calls it has received; during the interim, it is analyzing the situation to determine if it can restore service with other lines and reroute the electricity until it receives reports from personnel in the field to determine the extent of the damage (N.T. 73, 81-82).

- If it waited until its personnel inspected all downed lines before re-energizing its lines, Duquesne Light contends it would take weeks to restore service after a severe storm, because other lines are down as well, including telephone and cable television lines (N.T. 74, 85).

- During an outage, Duquesne Light opines its first priority is public safety.  Then, it tries to restore service to meet critical customers, hospitals, police departments and water pumping stations.  Then, it tries to restore service to the biggest block of customers that it can.  Finally, it tries to restore service to all other customers (N.T. 82).

- Duquesne Light is upgrading its transmission system to meet the requirements of the FERC and PJM, and to increase service reliability to its customers.  If a transmission line goes down, it wants to reduce the potential for overload on other lines.  It is trying to eliminate the 69 kV transmission line class (N.T. 90-91).

- The 69 kV Colfax-Highland transmission line was built in the late 1920s and appears to have been re-conducted around 1960 (N.T. 90-91).

- Duquesne Light began planning an upgrade to the 69 kV Colfax-Highland transmission line over two years ago (N.T. 91).

- Pursuant to 52 Pa. Code §57.72(d)(1)(i) and (v), Duquesne Light filed a Letter of Notification with the Commission at Docket No. A-2008-2077194 in November 2008 relating to the upgrade of the 69 kV Colfax-Highland transmission line, which became the Logans Ferry-Highland transmission line (N.T. 92, 109-10; Respondent’s Exh. 4).

- No protests were filed to the Letter of Notification (N.T. 93).

- By Order entered January 22, 2009 at Docket No. A-2008-2077194, the Commission approved the Letter of Notification (N.T. 94, 109; Respondent’s Exh. 5).

- The existing 69 kV Colfax-Highland transmission line consisted of a steel lattice tower arrangement with three conductors for the 69 kV lines with two shield wires above (N.T. 94, 96; Respondent’s  Exh. 6).

- The upgrade project will entail removing the existing steel tower and foundation and replacing it with a concrete foundation and a steel pole.  Each pole will carry double circuit 138 kV lines, i.e., three conductors on the left side and three conductors on the right side with two shield wires above  (N.T. 95-96; Respondent’s Exh. 6).

- Duquesne Light opines its new transmission line will exceed the requirements of the National Electrical Safety Code (“NESC”) (N.T. 101, 110).

- Duquesne Light submitted a construction drawing for the new 138 kV transmission line showing the McLafferty property in relation to the line (N.T. 102-03; Respondent’s Exh. 7).

- At maximum operating temperature, Duquesne Light estimates the lines will be 50 feet above the McLafferty property (N.T. 103, 107-09; Respondent’s Exh. 7).

- The previous steel lattice towers supporting the 69 kV transmission line were 85 feet in height; the new steel poles supporting the 138 kV transmission line will be at least 50 feet higher (N.T. 107).

- Each of the steel poles supporting the new 138 kV transmission line will vary in height depending upon its location (N.T. 107).

- The total length of the 138 kV transmission line is nine miles (N.T. 103).

- A Duquesne Light engineer, who is also a volunteer fireman, provides training to fire departments on how to safely work around downed power lines (N.T. 104).

- Duquesne Light has finished demolition of the old 69 kV transmission line and has begun installing foundations for the poles supporting the new 138 kV transmission line (N.T. 105).

- Based on its experience, Duquesne Light opines the greatest cause of outages on transmission lines is contact with trees (N.T. 104).

- Duquesne Light is clearing trees on the floor and sides of the proposed 138 kV transmission line in order to provide safe and reliable service (N.T. 114, 116-18).

- Trees contribute to power outages by either falling into the lines or growing into them from underneath or from the side, thus causing a phase to phase interruption or a phase to ground interruption (N.T. 115, 119).

- The NESC does not specify minimum requirements for vegetation clearance from power lines (N.T. 118-19, 124-26).

- Duquesne Light opines that trees beneath power line conductors should be removed, because they pose a maintenance risk and the rights-of-way need to be accessible (N.T. 122-25, 130).

- With this project, Duquesne Light is working with homeowners and local nurseries to replant lower growing, compatible vegetation species at no cost to the homeowners to replace trees that it removes (N.T. 127).

DISCUSSION

Complainant presents a number of issues for consideration, all of which arise from Respondent’s upgrading its transmission facilities running across his property.  Duquesne Light proposes to upgrade its existing 69 kV transmission line to a 138 kV transmission line by replacing existing structures with higher capacity facilities and engaging in vegetation maintenance.  We will review each of these issues seriatim.

A.	Jurisdiction

First, Complainant challenges the lawfulness of Respondent’s proposed facilities upgrade as exceeding the 1927 grant of easement allowing Duquesne Light to run its facilities across his property (N.T. 9-10).  As a creature of legislation, the Commission possesses only the authority the State Legislature has specifically granted to it in the Public Utility Code (the “Code”), 66 Pa. C.S. §§101, et seq.  Its jurisdiction must arise from the express language of the pertinent enabling legislation or by strong and necessary implication therefrom.  Feingold v. Bell of Pa., 477 Pa. 1, 383 A.2d 791 (1977); Allegheny County Port Authority v. Pa. P.U.C., 427 Pa. 562, 237 A.2d 602 (1967); Behrend v. Bell of Pa., 257 Pa. Superior Ct. 35, 390 A.2d 233 (1978); Pa. Department of Highways v. Pa. P.U.C., 198 Pa. Superior Ct. 87, 182 A.2d 267 (1962); City of Erie v. Pa. Electric Co., 383 A.2d 575 (Pa. Cmwlth. 1978).  The Commission, however, does not have jurisdiction to determine the scope and validity of an easement.  Fairview Water Company v. Pa. P.U.C., 509 Pa. 384, 502 A.2d 162 (1985).  Only a Court of Common Pleas sitting in equity can hear the easement claim.  Id.  Therefore, this claim can receive no consideration in this forum.

Likewise, the Commission has no jurisdiction to hear Complainant’s claim that he should be entitled to monetary compensation for any damages to his trees or property as a result of Respondent’s vegetation maintenance practices associated with this transmission line upgrade project.  Nothing in the Code confers jurisdiction upon the Commission to award monetary damages.  Accordingly, the Commission possesses no jurisdiction to consider the Complainant’s request for monetary damages.  See, DeFrancesco v. Western Pennsylvania Water Company, 499 Pa. 374, 453 A.2d 595 (1982); Elkin v. Bell of Pa., 491 Pa. 123, 420 A.2d 371 (1980); and Feingold, supra.

B.	Notification

Next, Complainant asserts Duquesne Light began this project without giving the public an opportunity to comment and without informing the affected property owners of the inherent dangers posed by high-power lines.  The record clearly shows, however, that on September 19, 2008, Duquesne Light sent to local public officials and affected property owners a letter informing them of the proposed transmission line upgrade project and inviting them to two informal public workshops on September 29-30, 2008.  It provided information at these workshops relating to right-of-way, transmission line location, vegetation management construction, engineering, public safety, energy efficiency, and a need for the line (N.T. 34-35, 91-93; Respondent’s Exh. 1).  Complainant attended both workshops (N.T. 35).

Furthermore, Duquesne Light filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(1)(i) and (v) with the Commission at Docket No. A-2008-2077194 in November 2008 relating to the proposed upgrade of this transmission line (N.T. 92, 109-10; Respondent’s Exh. 4).  Section 57.72(d)(1) allows an electric public utility to file a Letter of Notification in lieu of filing a formal siting application for the following:

(i)	An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character design or configuration of the proposed HV line does not substantially alter the right-of-way.

(ii)	An HV line which is proposed to be located entirely within a public road.

(iii)	An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and on the property of the sole customer to be served by the line, so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv)	A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

(v)	An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi)	An HV line having a proposed route of 2 miles or less.

(Emphasis added).  Clearly, Duquesne Light met the requirements of Section 57.72(d)(1)(i) and (v) in the present situation.

Duquesne Light served the affected property owners, including Complainant, with notice of its filing the Letter of Notification (Respondent’s Exh. 4).  No protests were filed (N.T. 93).  By Order entered January 22, 2009 at Docket No. A-2008-2077194, the Commission approved the Letter of Notification (N.T. 94, 109; Respondent’s Exh. 5).  Accordingly, Duquesne Light followed all applicable procedures in obtaining Commission approval for upgrading this transmission line.

Next, Complainant raises several issues relating to the safety of Respondent’s service and facilities.

C.	The Legal Standard

Section 1501 of the Code, 66 Pa. C.S. §1501, mandates that a public utility must furnish and maintain adequate, efficient, safe, and reasonable service and facilities, and must make such repairs, changes, alterations, substitutions, and improvements in or to such service and facilities as shall be necessary or proper for the accommodation, convenience and safety of its patrons and the public.  Upon finding that the service or facilities of a public utility are unreasonable, unsafe or inadequate, the Commission may prescribe, by regulation or order, the reasonable, safe and adequate service or facilities that a public utility must furnish or employ.  66 Pa. C.S. §1505.  Section 102 of the Code, 66 Pa. C.S. §102, defines “service” as:

Used in its broadest and most inclusive sense, includes any and all acts done, rendered, or performed, and any and all things furnished or supplied, and any and all facilities used, furnished, or supplied by public utilities . . . .

(Emphasis added).  A utility’s “service” is not merely confined to the distribution of utility service, but also includes “any and all acts” related to that function.  West Penn Power Co. v. Pa. P.U.C., 578 A.2d 75 (Pa. Cmwlth. 1990).  Further, Section 102 of the Code defines “facilities” in pertinent part as:

All the plant and equipment of a public utility, including all tangible and intangible real and personal property without limitation, and any and all means and instrumentalities in any manner owned, operated, leased, licensed, used, controlled, furnished, or supplied for, by, or in connection with, the business of any public utility.

As the party challenging the reasonableness, adequacy and safety of Respondent’s service and facilities, Complainant bears the burden of proof.  66 Pa. C.S. §332(a).

D.	The Burden of Proof

The term “burden of proof” means a duty to establish a fact by a preponderance of the evidence.   Se-Ling Hosiery v. Margulies, 364 Pa. 45, 70 A.2d 854 (1954); and Feinstein v. Philadelphia Suburban Water Company, 50 Pa. P.U.C. 300 (1976).  The term “preponderance of the evidence” means one party must present evidence that is more convincing, by even the smallest amount, than the evidence presented by the other party.   Id.  Accordingly, one must review the record in this case to determine whether Complainant has satisfied his burden of proof.  If the review indicates the burden has been satisfied, one must then determine whether Respondent has submitted evidence of co-equal value or weight to refute Complainant’s evidence.  If this has occurred, the burden of proof cannot be satisfied, unless the party bearing the burden of proof presents additional evidence.  Morissey v. Pa. Dept. of Highways, 424 Pa. 87, 225 A.2d 895 (1967); and Burleson v. Pa. P.U.C., 443 A.2d 1373 (Pa. Cmwlth. 1982), affirmed, 501 Pa. 443, 461 A.2d 1234 (1983).

Furthermore, substantial evidence must support the Commission’s decision.   See, e.g., Section 704 of the Administrative Agency Law, 2 Pa. C.S. §704; and Yellow Cab Company v. Pa. P.U.C., 524 A.2d 1069 (Pa. Cmwlth. 1987).  The term “substantial evidence” means such relevant evidence that a reasonable mind may accept as adequate to support a conclusion.  More is required than a mere trace of evidence or a suspicion of the existence of a fact sought to be established.  Norfolk & Western Ry. Co. v. Pa. P.U.C., 489 Pa. 109, 413 A.2d 1037 (1980); Erie Resistor Corp. v. Unemployment Comp. Bd. of Review, 194 Pa. Superior Ct. 278, 166 A.2d 96 (1961); and Murphy v. Pa. Dept. of Public Welfare, White Haven Center, 480 A.2d 382 (Pa. Cmwlth. 1984).  Moreover, in order to establish a sufficient case against a utility to satisfy the burden of proof, a complainant must show the utility is responsible or accountable for the problem described in the complaint.  Feinstein, supra.

E.	Public Safety

The existing transmission line is either over a corner of Complainant’s house or in close proximity to it (N.T. 9; Complainant’s Exh. 1; Respondent’s Exh. 2).  Complainant points to three incidents where this transmission line has fallen, twice landing on his roof.  These incidents happened in December 1991, May 1998 and June 2000 (N.T. 10-13, 15, 35-38).   The May 1998 incident occurred during a storm or severe weather.  The cause of the other incidents is unknown (N.T. 12-13, 15, 67, 70-71, 77-79; Respondent’s  Exh. 3).  Complainant faults Duquesne Light for the manner in which it responds to such emergencies, for relying upon untrained police, fire and emergency personnel to respond to these emergencies, and for blindly re-energizing such lines without regard to public safety.

No one questions the fact that the standard of care imposed upon a supplier of electrical power, particularly when that power is supplied at high voltage, is among the highest recognized in the law.  Slater v. Pennsylvania Power Company, 383 Pa. Superior Ct. 509, 557 A.2d 368 (1989); Densler v. Metropolitan Edison Company, 235 Pa. Superior Ct. 585, 345 A.2d 758 (1975).  A supplier of electrical current is bound not only to know the extent of the danger, but to use the very highest degree of care practicable to avoid injury to everyone, who may be lawfully in proximity to its wires and liable to come accidentally or otherwise in contact with them.  Brillhart v. Edison Light & Power Co., 368 Pa. 307, 312, 82 A.2d 44 (1951); Fitzgerald v. Edison Electric Illuminating Co., 200 Pa. 540, 543, 50 A. 161 (1901).  That a transmission line is a dangerous instrumentality is recognized everywhere.  No matter where located it is a source of grave peril and the law requires that the possessor of such an instrumentality exercise a high degree of care.  Yoffee v. Pa. Power & Light Co., 385 Pa. 520, 536, 123 A.2d 636 (1956).

Complainant avers Duquesne Light violates this standard of care by having inadequate personnel to respond appropriately to incidents involving downed power lines (N.T. 16-18, 28-29, 139-40).  Mr. McLafferty wants the Commission to require Duquesne Light to have sufficient personnel on duty, who are trained and equipped to respond to these emergencies (N.T. 29-30).

Nothing in the record supports the assertion that Duquesne Light employs insufficient personnel to assure public safety.  As one would reasonably expect, Duquesne Light’s response time to a report of a line down will depend upon the number of calls it receives during a given time (N.T. 73).  During a storm, it may receive as many as 100 calls within 10 minutes reporting lines down (N.T. 73, 84).  Duquesne Light personnel may take anywhere from 10 minutes to one-half hour to respond to a report of a downed line depending upon the number of calls it receives; during the interim, it is analyzing the situation to determine if it can restore service with other lines and reroute the electricity until it receives reports from personnel in the field to determine the extent of the damage (N.T. 73, 81-82).  If it waited until its personnel inspected all downed lines before re-energizing its lines, Duquesne Light contends it would take weeks to restore service after a severe storm, because other lines are down as well, including telephone and cable television lines (N.T. 74, 85).  During an outage, Duquesne Light opines it tries to restore service to meet the needs of critical customers, hospitals, police departments and water pumping stations first.  Then, it tries to restore service to the biggest block of customers that it can.  Finally, it tries to restore service to all other customers (N.T. 82).

Duquesne Light has about 100 69 kV, 138 kV and 345 kV transmission lines covering approximately 600 miles in its service territory (N.T. 67).  In the last 11 years, it had five instances where transmission line conductors came down (N.T. 67).  It is unaware of any catastrophic personal injury or property damage resulting from downed transmission lines in the last 28 years (N.T. 62, 68, 79).

Duquesne Light linemen are trained to handle a downed and energized 4 kV distribution line, but they cannot handle a downed and energized 69 kV transmission line.  The 69 kV transmission line must be de-energized first (N.T. 68, 87).  Assuming it is not automatically de-energized, to manually de-energize the 69 kV Colfax-Highland transmission line crossing the McLafferty property, a Duquesne Light operator must go to the Colfax substation, open the switch and lock it open, then perform the same function at the Highland substation at the other end of the line (N.T. 68-69).  After the 69 kV transmission line is de-energized, it is then safe for linemen to work on it (N.T. 69).

One would reasonably expect fire, police and emergency medical personnel to be among the first responders in case of a fallen line, since they are based in the local community.  Once alerted, Duquesne Light personnel, who are more widely dispersed, would normally respond to the scene somewhat later.  No evidence in this record suggests insufficient Duquesne Light personnel are employed to respond to these emergencies or that they are unreasonably tardy or poorly trained.

In the event of a fallen line, automatic protective equipment on the line attempts to isolate the problem and de-energize that portion of the line; then automatic reclosure equipment in the field and the substation attempts to re-energize the line to restore service.  The same process occurs when a transmission line falls into a distribution line.  This breaker/reclosure operation occurs automatically two or three times before the line is finally de-energized.  A reclosure on a 69 kV transmission line operates automatically once in an attempt to re-energize the line before it finally stays open.  This practice follows Duquesne Light’s experience that 80% of all faults are temporary.  Since all of its lines are un-insolated and western Pennsylvania is heavily treed, giving the breakers a chance to de-energize and then reclose will oftentimes restore service automatically, for example after car accidents or when tree branches contact the lines in wind storms (N.T. 65-67, 71-72, 75, 86, 97).

This system was called into play on May 19, 1998 at 8:14 p.m., when a tree fell into the 69 kV Colfax-Highland transmission line, which in turn fell into the 4 kV distribution circuit running along Earlwood Road, during a storm (N.T. 70-71, 77-79; Respondent’s Exh. 3).  During this event, a reclosure device on the 4 kV distribution circuit opened and closed automatically several times in order to isolate the fault and re-energize the line before it stayed open and locked out; service was restored at 3:30 a.m. (N.T. 71, 77-79; Respondent’s Exh. 3).  Duquesne Light has no record of re-energizing the 69 kV transmission line before the fault condition was cleared (N.T. 83).  Importantly, Duquesne Light cut out the reclosures on this 69 kV transmission line in 1976, so they could not have reclosed and re-energized the line during the May 1998 event as Complainant feared.  Once the breakers operated in 1/10 of a second, the 69 kV transmission line would have remained locked out and de-energized (N.T. 98-100).  Duquesne Light hypothesizes that the only way for the 69 kV transmission line to become re-energized after the breakers locked out on May 19, 1998 was by contact with the live 4 kV distribution line, until it also became locked out (N.T. 98-99).

Accordingly, nothing in this record supports Complainant’s assertion that Respondent disregards public safety when re-energizing its lines.

Similarly, Complainant fails to articulate what training he believes Respondent does not provide fire, police and emergency medical personnel that it should.  He asserts Duquesne Light depends upon fire, police and emergency medical personnel to respond to emergencies involving its transmission line facilities, but it does not train them on how to deal with these situations (N.T. 13-14, 17-18, 29, 140).  As discussed previously, in the last 11 years, Duquesne Light had five instances where transmission line conductors came down (N.T. 67).  Moreover, even Duquesne Light personnel cannot handle a downed 69 kV transmission line before it is de-energized (N.T. 68, 87).  So, one would not reasonably expect non-utility personnel to perform such work.

To reiterate, if a fault condition occurs on a transmission line, such as a downed line or a tree falling into a line, an automatic breaker operation will de-energize the line after attempting to re-energize the line one time (N.T. 65-67, 71-72, 75, 86, 97).  So chances of contact with a downed energized transmission line are minimal at best.  Duquesne Light is unaware of any catastrophic personal injury or property damage resulting from downed transmission lines in the last 28 years (N.T. 62, 68, 79).  Finally, a Duquesne Light engineer, who is also a volunteer fireman, provides training to fire departments on how to safely work around downed power lines (N.T. 104).  Hence, Complainant’s bald assertion, without more specifics, relating to a need for training finds no support in this record.

F.	Vegetation Maintenance

Lastly, Complainant wants the Commission to direct Duquesne Light to preserve his trees slated for removal as part of this proposed upgrade project (N.T. 28).  Mr. McLafferty believes the trees that Duquesne Light now wishes to remove saved his wife and family from personal injury and his home from destruction during the fallen power line incidents he recites (N.T. 13, 16, 20, 28-29, 139).  Clearly, how a public utility engages in its vegetation maintenance practice falls with the parameters of its service obligation under the Public Utility Code.  West Penn Power, supra.

Based on its experience, Duquesne Light opines the greatest cause of outages on transmission lines is contact with trees (N.T. 104).  Trees contribute to power outages by either falling into the lines or growing into them from underneath or from the side, thus causing a phase to phase interruption or a phase to ground interruption (N.T. 115, 119).  Duquesne Light wants to clear trees on the floor and sides of the proposed 138 kV transmission line in order to provide safe and reliable service (N.T. 114, 116-18).  It opines that trees beneath power line conductors should be removed, because they pose a maintenance risk and the rights-of-way need to be accessible (N.T. 122-25, 130).

As part of its vegetation maintenance practice, Duquesne Light selectively removes any trees under its transmission lines that have the potential to reach the conductors from underneath (N.T. 44, 61).  It has cut or trimmed all of the trees in the right-of-way along the route of the proposed transmission line project, except for the trees on Complainant’s property (N.T. 53).  Duquesne Light wants to remove five trees that are underneath its transmission line on Complainant’s property, i.e., a pin oak, a spruce, two sugar maples, and a basswood (N.T. 44-53, 120-21; Respondent’s Exh. 2).  Mr. McLafferty agreed to allow Duquesne Light to remove all of these trees except the pin oak, which is situated in front of his house along Earlwood Road (N.T. 53, 57-58; Respondent’s Exh. 2).  Duquesne Light considers the pin oak to be a very prolific grower, capable of interfering with its transmission line (N.T. 49-50, 120-21; Respondent’s Exh. 2).

Duquesne Light explains all of the selected trees may grow anywhere from 70 to 100 feet tall and possess the potential to contact the transmission line conductors, which will be 70-80 feet above ground; some species are capable of growing to 120 feet in height (N.T. 54, 56, 120-21, 127).  The previous steel lattice towers supporting the 69 kV transmission line were 85 feet in height; the new steel poles supporting the 138 kV transmission line will be at least 50 feet higher (N.T. 107).  Each of the new steel poles will vary in height depending upon its location (N.T. 107).  Of critical significance, however, is the fact that at maximum operating temperature, the lines will only be 50 feet above the McLafferty property (N.T. 103, 107-09; Respondent’s Exh. 7).  Thus, one can readily see that the five trees selected for removal here possess the potential to interfere with the proposed transmission line.  Moreover, they can likewise interfere with maintenance and repair crews working in the right-of-way.  Thus, Respondent’s vegetation maintenance practice as it relates to Complainant’s property appears reasonably necessary for the convenience and safety of its patrons, employees and the public.  66 Pa. C.S. §1501.

G.	Summary

For all of the foregoing reasons, the complaint lacks merit and will be denied.

CONCLUSIONS OF LAW

- The Commission has jurisdiction over the subject matter and the parties to this proceeding to the extent discussed in the foregoing decision.  66 Pa. C.S. §701.

- The Commission does not have jurisdiction to determine the scope and validity of an easement.  Fairview Water Company v. Pa. P.U.C., 509 Pa. 384, 502 A.2d 162 (1985).

- The Commission possesses no jurisdiction to award monetary damages.  DeFrancesco v. Western Pennsylvania Water Company, 499 Pa. 374, 453 A.2d 595 (1982); Elkin v. Bell of Pa., 491 Pa. 123, 420 A.2d 371 (1980); Feingold v. Bell of Pa., 477 Pa. 1, 383 A.2d 791 (1977).

- Complainant has failed to meet his burden of proving that he is entitled to the relief he is seeking from the Commission.  66 Pa. C.S. §332(a).

ORDER

THEREFORE,

IT IS ORDERED:

That the complaint of William McLafferty against Duquesne Light Company at Docket No. C-2009-2101144 is hereby denied.

Dated: September 9, 2009

John H. Corbett, Jr.

Administrative Law Judge

C-2009-2101144  William McLafferty v. Duquesne Light Company

William McLafferty

121 Earlwood Road

Pittsburgh PA  15235

412.793.6755

Krysia  Kubiak

Duquesne Light Company

411 Seventh Avenue

Mail Drop 16-1

Pittsburgh PA  15219

412.393.6505

The 69 kV transmission line was in place on Complainant’s property when the house was built in 1945 (N.T. 34).

No action may be maintained for any action claimed to be in violation of the Public Utility Code that is alleged to have occurred more than three years before the complaint is filed.  66 Pa. C.S. §3314.  But here, Complainant is alleging ongoing unsafe practices by Respondent.