PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held March 25, 2010
Commissioners Present:

James H. Cawley, Chairman

      Tyrone J. Christy, Vice Chairman
Wayne E. Gardner 

Robert F. Powelson

Letter of Notification of PPL Electric 
Utilities Corporation, filed pursuant to 
52 Pa. Code Chapter 57.72, with respect 




A-2010-2154494
to a Section of the Monroe-Jackson #2 138 kV
Transmission Line and the Stroudsburg 

#1& #2 138 kV Tap Lines in the Borough
of Stroudsburg, Monroe County, PA.
ORDER

BY THE COMMISSION:

On January 22, 2010, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

            (ii)       An HV line which is proposed to be located entirely within a public road.

(iii)  An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present           levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.
(v)  An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vi)    An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with

Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Monroe County Commissioners, Monroe County Planning Commission, Stroudsburg Borough, Stroudsburg Borough Council and Stroudsburg Borough Planning Commission, as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PPL Electric seeks the Commission’s approval for the siting and construction of (1) approximately 275 feet (three spans) of new 138 kV transmission line 
around the existing Stroudsburg Substation and (2) the Stroudsburg #1 and #2 138 kV Tap Lines in the Borough of Stroudsburg, Monroe County, Pennsylvania (collectively, the “Project”).  
PPL Electric proposes to construct approximately 275 feet (three spans) of new 138 kV transmission line around the existing Stroudsburg Substation.  This new section of single-circuit 138 kV transmission line will be constructed to connect the existing Martins Creek-Stroudsburg 138/69 kV Transmission Line to the existing Jackson-Stroudsburg 138/69 kV Transmission Line.  The combination of this new section and the existing lines will be called the Monroe-Jackson #2 138 kV Transmission Line.  The existing Monroe-Jackson 138 kV Transmission Line will be renamed the Monroe​-Jackson #1 138 kV Transmission Line.  The construction of the 275 feet (three spans) of new 138 kV transmission line will require the installation of three steel pole structures, which will be approximately 75 feet in height.  The new section of transmission line will consist of three 556.5 thousand circular mills (kcmil), 24/7 stranding, aluminum conductor steel reinforced (“ACSR”) power conductors.  One 3/8-inch steel overhead ground wire will be installed to provide lightning protection for the proposed line. 

 
 
PPL Electric also plans to construct two new single-circuit 138 kV tap lines into the existing Stroudsburg Substation to source the proposed 138-12 kV transformers.  The new tap lines will be called the Stroudsburg #1 and #2 138 kV Taps. The Stroudsburg #1 138 kV Tap will be approximately 110 feet in length.  This tap will require the installation of one steel pole structure, which will be approximately 65 feet in height.  The Stroudsburg #2 138 kV Tap will be approximately 25 feet in length.  This tap will share one steel pole structure with the Monroe-Jackson #2 138 kV Transmission Line.  Both tap lines will consist of three 556.5 kcmil, 24/7 stranding, ACSR power conductors and one overhead ground wire.  The steel overhead ground wires will be installed to provide lightning protection for the proposed tap lines. 


 
PPL Electric states that the Project is part of PPL Electric's overall long-term Plan for the heavily-loaded service area of the Southern Pocono region.  The conversion is required to increase service reliability by relieving overloading of a nearby transmission line and low voltage issues in the area.  The Plan calls for converting the existing 69 kV facilities in the Southern Pocono area to 138 kV operation.  Increasing the operating voltage from 69 kV to 138 kV will double the capacity of the existing transmission lines and substations and will enable PPL Electric to continue to provide reliable electric service to its customers without establishing additional major transmission corridors.  Construction of the Stroudsburg 138 kV Taps and the new 138 kV spans around Stroudsburg Substation is a necessary part of the Plan. 

In addition, PPL Electric states that the Completion of this project will allow PPL Electric to remain in compliance with North American Electric Reliability Corporation (“NERC”) Transmission Planning Standards (“TPL”) and PPL Electric’s Reliability Principles and Practices (“RP&P”).
PPL Electric states that the Project will be located entirely on land owned by PPL Electric.  No additional right-of-way is required.  PPL Electric also states that proposed Project will not create any unreasonable risk of danger to the public health or safety.  The Project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable NESC minimum standards and all applicable legal requirements.                 



The total estimated cost for the proposed work at Stroudsburg is approximately $2.65 million, which includes $1.75 million for the substation modifications and $900,000 for the transmission line work (i.e. design and construction of the Stroudsburg  #1and #2 Taps and the new 138 kV spans around Stroudsburg Substation).  This filing concerns only the proposed modifications of transmission facilities (i.e. $900,000), which are the only part of the project that requires prior Commission approval under 52 Pa. Code, Chapter 57, Subchapter G.  Construction is scheduled to commence in March 2010, to support an in-service date of November 2010. 
Upon review, the Commission finds that the PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the Tap Lines are less than two miles.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting.  We note that our approval of the Letter of Notification does not reach the issues of accounting treatment and cost recovery; THEREFORE,

IT IS ORDERED:


           That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to a Section of the Monroe-Jackson #2 138 kV Transmission Line and the Strroudsburg  #1& #2 138 kV Tap Lines in the Borough of Stroudsburg, Monroe County, PA, is hereby approved.

[image: image1.emf]

   BY THE COMMISSION,


   James J. McNulty


   Secretary
(SEAL)
ORDER ADOPTED: March 25, 2010
ORDER ENTERED: March 29, 2010
PAGE  
5

