PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held August 18, 2010
Commissioners Present:

James H. Cawley, Chairman

      Tyrone J. Christy, Vice Chairman 
John F. Coleman, Jr.

Wayne E. Gardner 

Robert F. Powelson

Letter of Notification of PPL Electric

Utilities Corporation filed pursuant to

52 Pa. Code Chapter 57 Subchapter G,                                                  A-2010-2172213

With respect to the Hawley #1 & #2 

138/69 kV Transmission Tap Line in 

Palmyra Township, Wayne County, 

Pennsylvania.

ORDER

BY THE COMMISSION:

On April 26, 2010, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.
            (ii)       An HV line which is proposed to be located entirely within a public road.

(iii)  An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present           levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.

(v)  An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vi)    An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Wayne County Commissioners, Wayne County Planning Commission, Palmyra Township Board of Supervisors, and Palmyra Township Planning Commission .  No protests were filed.  No hearings were held.  


PPL Electric proposes to construct the double-circuit Hawley Taps, which will be approximately 250 feet in length and will connect the existing Blooming Grove- Honesdale 69 kV Transmission Line with the proposed Hawley Substation in Palmyra Township, Wayne County, Pennsylvania.  PPL Electric states that the proposed Hawley Taps, together with the Hawley Substation and distribution lines associated therewith, are required to improve reliability of service and meet increasing demand in the vicinity of Palmyra Township. 



PPL Electric states that the proposed Hawley Taps will be approximately 250 feet in length.  The taps will connect the existing Blooming Grove-Honesdale 69 Kv Transmission Line with the proposed Hawley Substation.  The purpose of the Hawley Taps, together with the proposed Hawley Substation, is to provide an additional source of supply to approximately 4,900 PPL Electric distribution customers located in the Palmyra Township area.  The Hawley Taps and Hawley Substation are needed because the present distribution facilities that supply PPL Electric's distribution customers in that area exceed the normal planning guidelines based on PPL Electric's Reliability Principles and Practices Manual ("RP&P").  The Hawley Taps and the proposed Hawley Substation will relieve thermal over loading, reduce the number of customers served from the existing distribution lines, and resolve reliability issues associated with the existing distribution lines serving that area. 

PPL Electric explains that presently, PPL Electric's distribution customers in this area are served from the Kimbles 69-12 kV Substation, the Lakeville 69-12 kV Substation, and the Tafton 66- 12 kV Substation via each substation's associated 12 kV distribution lines: the Kimbles 26-1, Lakeville 88-4, and Tafton 80-2 12 kV distribution lines.  There are no other 12 kV sources serving PPL Electric distribution customers in the Palmyra Township area.



The existing Kimbles 26-1 12 kV distribution line is projected to exceed the normal planning guidelines set forth in PPL Electric's RP&P in 2012.  The normal and emergency ratings of the 477 kcmil (thousands of circular mils)
 aluminum conductor of the Kimbles 26-1 12 kV distribution line are 11 MV A and 13 MV A, respectively.  The peak load on the distribution line forecasted for the winter of 2012 is 11.1 MVA. Overloading the Kimbles 26-1 12 kV line could result in conductor damage or failure. Further, as a result of the overloading, the existing distribution line cannot accommodate the future load growth expected in the Palmyra Township area. 
Additionally, as a result of the large number of customers experiencing multiple outages per year, the Kimbles 26-1 12 kV distribution line has repeatedly been among the worst performing circuits on the PPL Electric system. This is due to the length of the circuit, the rural nature of the area, and the high number of customers served by the line. 

Also, the existing system configuration has limited transfer capability for maintenance and other equipment outages because the adjoining substations and supply lines are heavily loaded.  Consequently, if the existing Kimbles 26-1 12 kV distribution line were to fail or require maintenance, approximately 2,000 customers would be out of service until the repairs could be completed. 
The Lakeville 88-4, Tafton 80-2, and Kimbles 26-1 12 kV distribution lines currently exceed PPL Electric's RP&P for the number of customers per feeder. The RP&P provides that no more than 1,300 customers should be served from a 12 kV circuit. However, these three circuits presently serve approximately 1,423, 1,690, and 2,000 customers, respectively.  

To alleviate these problems, PPL Electric plans to construct the new Hawley Substation and connecting distribution lines in the Palmyra Township area.  PPL Electric plans to construct and install two new 12 kV distribution facilities, the new Hawley 1 and Hawley 2 12 kV distribution lines, that will be connected to the Hawley Substation to serve customer load in the Palmyra Township area to relieve loading and increase reliability and operating flexibility.  The Hawley Substation and new 12 kV facilities will reduce peak loading on the existing Kimbles 26-1 12 kV distribution line by approximately 5.1 MVA.  Additionally, the new facilities will resolve the customer count violations on the existing Lakeville 88-4, Tafton 80-2, and Kimbles 26-1 12 kV distribution lines.  Once the proposed project has been completed, the above referenced lines will serve approximately 1,260, 1,160, and 1,120 customers, respectively, which are below the RP&P guideline of 1,300 customers per circuit.  In turn, the new Hawley 1 and Hawley 2 12 kV distribution lines will serve approximately 1,000 and 570 customers, respectively. 

PPL Electric states that the Hawley Substation will be supplied from the existing Blooming Grove-Honesdale 69 kV Transmission Line.  The Hawley Taps proposed herein will connect the Hawley Substation with the Blooming Grove-Honesdale 69 kV Transmission Line.  The Hawley Taps will be sited and designed as double circuit 138 kV transmission tap lines that will extend 250 feet from the Blooming Grove-Honesdale 69 kV Transmission Line to the proposed Hawley Substation.  The Hawley #1 Tap and transformer #1 will be constructed and connected to the Hawley Substation.  Initially, only a portion of the Hawley #2 Tap will be constructed and tied with the Hawley #1 Tap for operating flexibility.  This portion of the Hawley #2 Tap will be connected to a temporary mobile transformer at the Hawley Substation to relieve outages on transformer #1 as necessary.  The remaining portion of Hawley #2 Tap will not be constructed and connected to the Hawley Substation until a second transformer is installed when future load increases make it appropriate to do so. The proposed Hawley Taps are depicted in the aerial plot plan provided at the end of Attachment 2 to this LON.  The Hawley Taps will be designed and constructed for 138 kV operation, although they initially will operate at 69 kV. 

PPL Electric states that the Hawley Taps will require two steel mono-poles each of varying height.  The tap poles will be approximately 105 feet in height.  The remaining two poles will be approximately 65 feet in height.  All of the poles will be secured with anchor guys.  The proposed tap lines will each consist of three power conductors and one overhead ground wire.  The power conductors will be 556.5 kcmil, 24/7 strand ACSR.  The overhead ground wire will be 3/8-inch steel and will provide lightning protection for the proposed Tap Lines. 

PPL Electric states that the Hawley Taps will be designed to comply with, and will generally surpass, the applicable minimum standards in the National Electrical Safety Code (NESC).
The total estimated cost to design and construct the proposed project is $2.1 million, which includes the cost of the Hawley Substation and the distribution work related thereto, and the estimated $530,000 cost for the proposed Hawley Taps.  Construction is scheduled to commence in august 2010, for an in-service date of November 2011.
PPL Electric states that because the proposed Hawley Taps will be only 250 feet in length and will be installed in the vicinity of existing transmission lines, as depicted in an aerial plot plan at the end of Attachment 2 to this LON, it is anticipated that the Hawley Taps will have minimal incremental impacts on the area.  The proposed 4.0 acre site for the Hawley Substation is traversed by the existing Blooming Grove-Honesdale 69 kV Transmission Line.  The site is zoned for Residential use and is currently a wooded parcel.  The parcel is bordered on the north, east, and west sides by wooded parcels, and is bordered on the south by a combination of wooded and commercial properties.

PPL Electric states that the proposed Hawley Taps will not create any unreasonable risk of danger to the public health or safety. The Hawley Taps will be designed, constructed, operated, and maintained in a manner that meets or surpasses all applicable National Electrical Safety Code (“NESC”) minimum standards and all applicable legal requirements.
PPL Electric states that the proposed Hawley Taps will be located entirely on the site for the Hawley Substation, which is owned in fee by PPL Electric.  As a result, no additional rights-of-way are necessary for the proposed Hawley Taps. 



PPL Electric states that the Hawley Taps were reviewed with representatives from Palmyra Township and Wayne County.  The Township and the County have no objection to the Hawley Taps. 
Upon review, the Commission finds that the PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the lengths of the transmission lines to be constructed as part of the Project are less than two miles.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission 
policy regarding transmission line siting; THEREFORE,

IT IS ORDERED:


           That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the Hawley #1 & #2 138/69 kV Transmission Taps in Palmyra Township, Wayne County, PA, is hereby approved.

[image: image1.png]



BY THE COMMISSION,


Rosemary Chiavetta

Secretary
(SEAL)
ORDER ADOPTED: August 18, 2010
ORDER ENTERED: August 23, 2010
� A circular mil is the cross-sectional area of a wire one mil in diameter, where 1 kcmil= 0.5067 mm2





PAGE  
8

