PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held February 10, 2011
Commissioners Present:

James H. Cawley, Chairman

      Tyrone J. Christy, Vice Chairman

John F. Coleman, Jr.

Wayne E. Gardner 

Robert F. Powelson

Letter of Notification of PECO Energy
Company filed pursuant to 52 Pa. Code
Chapter 57 Subchapter G, with respect to                                                                           the Reconductoring and Reconfiguration                                             A-2010-2205618             of the Buckingham-Pleasant Valley 230                                                                                  kV Transmission Line located in Solebury
Township, Borough of New Hope, and
Buckingham Township, Bucks County, PA.

ORDER

BY THE COMMISSION:

On October 20, 2010, PECO Energy Company (“PECO”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(i) and (v)of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

            (ii)       An HV line which is proposed to be located entirely within a public road.

(iii)  An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present           levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.

(v)  An HV line which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vi)    An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Chief Executive Officers, Boards of Supervisors and Land Use Planning Officers of Solebury Township, Borough of New Hope, Buckingham Township, Bucks County; and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PECO seeks the Commission’s approval to reconductor and reconfigure, build and modify, entirely on existing right-of-way and fee-owned or easement land, approximately 8.4 miles of 230kV transmission line located in Solebury Township, Borough of New Hope, and Buckingham Township, Chester County, Pennsylvania.  
PECO states that this project will be done in coordination with a related PSE&G transmission project; PECO will do the work to its tower 47-3 at the Pennsylvania -New Jersey state line, and PSE&G will do work from that point on to the PSE&G Pleasant Valley Substation.  According to PECO, this transmission line work is necessary to maintain and improve the reliability of the interstate transmission grid.  The need for transmission line modifications was identified in the 2006 Baseline Regional Transmission Planning Report (the “2006 Baseline RTEP Report”) prepared by the PJM
 Interconnection LLC (“PJM”), and in subsequent interactions with PJM.

PECO explains that in the course of its ongoing review of the interstate transmission system, PJM has determined that, beginning in the summer of 2011, the Buckingham-Pleasant Valley 230 kV transmission line will be loaded at 112% of design capacity during N-2 contingency operations if certain portions of the 500 k V interstate transmission system are out of service.  The PJM 2006 Baseline Report (which is attached to this filing as Exhibit A) states (p. 5) that the “recommended solution is to reconductor the Buckingham-Pleasant Valley 230 kV circuit by June 2011.”  PECO states that this statement in the PJM Baseline Report constitutes approval by PJM of the noted “recommended solution” as a reliability modification to the transmission system.  Further, pursuant to Schedule 6, Section 1.7 of PJM's Operating Agreement, which was approved by, and is on file with, the Federal Energy Regulatory Commission (“PERC”), once PJM has approved reliability modifications to the transmission system, PECO is required to make those modifications. 



PECO states that the Buckingham-Pleasant Valley line is an existing 230 kV circuit on an active transmission right-of-way.  The PECO portion of this line, going from PECO's Buckingham Substation to tower 47-3 at the Pennsylvania/New Jersey state line, is primarily through rural areas in Bucks County.  Further, PECO states that the general line modification needed for this project is to reconductor the line with new conductors of higher capacity so that the projected load may safely and reliably be transmitted over the line in the event of a contingency outage on certain 500 kV transmission lines.  Also, some of the existing towers may require modification in order to safely support the new heavier conductors. 

PECO states that the design criteria used for the transmission line work described herein is set forth in the PECO's standards for transmission line construction. These design criteria meet or exceed the requirements of the National Electrical Safety Code ("NESC").  Furthermore, PECO will construct, operate and maintain the transmission facilities in a manner that satisfies or surpasses NESC standards.  The proposed project will not create an unreasonable risk of danger to the public health or safety. 


PECO states that the functional requirements of the project allow it to use existing rights-of-way and fee-owned or easement land for all of the modifications for this project.  The transmission line work will take place on an existing transmission line right-of-way, which has been used as a power line corridor for many years and the work will primarily use existing support structures.  Before it performs construction work, 
PECO will conduct an analysis of the presence /absence of wetlands for the project.  Where wetlands are identified and access is required, they will be surveyed, marked in the field, and designated on drawings.  Where access over wetlands is necessary to perform the construction work, PECO will utilize temporary mats or other approved or permitted methods to avoid damage.  As a consequence of all of these factors, the transmission line modifications proposed for approval herein will create minimal new environmental and land use impacts. 



PECO states that the total cost for the transmission line work associated with the project is estimated to be $4,670,000.   This project has a needed in-service date of June 1, 2011 in order to meet the requirements of the PJM 2006 Baseline Report.   In order to meet this in-service date, PECO needs to commence construction in February 2011. 


Upon review, the Commission finds that the PECO’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(i) and (v) because the line is being reconductored and reconstructed entirely on an existing transmission line right-of-way, and the size, character, design, or configuration, of the proposed HV line will not substantially alter the right-of-way of the existing HV line associated with the project.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,
IT IS ORDERED:


           
That the Letter of Notification filed by PECO Energy Company for the Buckingham-Pleasant Valley 230 kV Transmission Line located in Solebury Township, 
Borough of New Hope, and Buckingham Township, Bucks County, PA, is hereby approved.

[image: image1.png]



 

   BY THE COMMISSION,


   Rosemary Chiavetta

   Secretary

 (SEAL)

ORDER ADOPTED: February 10, 2011
ORDER ENTERED: February 10, 2011
� PJM is the Independent System Operator ("ISO") for the transmission system in the Mid-Atlantic region and NERC-registered Transmission Operator, Transmission Planner, Reliability Coordinator, Transmission Provider and Balancing Authority for the PECO transmission system.





PAGE  
6

