PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held February 10, 2011
Commissioners Present:

James H. Cawley, Chairman

      Tyrone J. Christy, Vice Chairman

John F. Coleman, Jr.

Wayne E. Gardner 

Robert F. Powelson

Letter of Notification of PECO Energy
Company filed pursuant to 52 Pa. Code
Chapter 57.72, with respect to the
Reconductoring and Reconfiguration                                             A-2010-2203891
of the Doe Run-Jennersville-Clay 230 kV                                                  
Transmission
 Line (the “Clay Tap”) located 
in Penn, New London, Upper Oxford and 

Franklin Townships, Chester County, PA.

ORDER

BY THE COMMISSION:

On October 7, 2010, PECO Energy Company (“PECO”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(i) and (v)of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

            (ii)       An HV line which is proposed to be located entirely within a public road.

(iii)  An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present           levels, so long as the size, character, design, or configuration of the          proposed HV line does not substantially alter the right-of-way.

(v)  An HV line which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vi)    An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with

Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, the Chief Executive Officers, Boards of Supervisors and Land Use Planning Officers of 
Penn, New London, Upper Oxford and Franklin Townships, Chester County Government, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PECO seeks the Commission’s approval to reconductor and reconfigure, build and modify, entirely on existing right-of-way and fee-owned or easement land, approximately seven (7) miles of 230kV transmission line located in Penn, New London, Upper Oxford and Franklin Townships, Chester County Pennsylvania.  

PECO states that this transmission line work is necessary to provide reliable electric service to PECO's distribution customers in the vicinity of the subject project.   PECO explains that it provides electric distribution service to customers in the immediate vicinity of Penn, New London and Franklin Townships, and some load in other nearby areas of Chester County, through its Clay Substation and Jennersville Power Delivery Module (“PDM”).  The Clay Substation and the Jennersville PDM are both served by the same transmission line - the 220-01 line, which in the seven-mile stretch from PECO's Doe Run switching station to its Clay Substation is a single-circuit radial transmission line known as the “Clay Tap.”  Because the Clay Tap is a single-circuit radial transmission line, the Clay Substation and Jennersville PDM currently have only one source of transmission service. 


Further, the load served by the Clay Substation and the Jennersville PDM is geographically located at the southern edge of PECO’s service territory, near the Pennsylvania-​Delaware border and the Pennsylvania-Maryland border.  When the Clay Substation and Jennersville PDM were originally constructed and installed, load in the area was of a magnitude such that, if the Clay Tap was out-of-service, the local distribution load could be switched to other services on the PECO 34 kV distribution system while repairs were made to the Clay Tap.  As long as load in the area remained relatively low, PECO could provide reliable distribution service using the Clay Tap as the primary source of service, and the 34 kV-distribution system, as the secondary source of service.  However, the local load has grown to the point where it will soon be impossible to serve the local distribution load using the 34 kV system as the contingency service option.   Presently, approximately 60 MVA of electric load is served by the Clay Substation, and approximately 20 MVA of electric load is served by the Jennersville PDM. With load at that magnitude, if transmission service via the Clay Tap was lost for any reason, it would be difficult or impossible to reconfigure the 34 kV-distribution system to supply the entire 60 or 80 MVA of load served by those two stations. 



PECO believes that this issue can be resolved by constructing a second 230 kV transmission source to serve the Clay Substation thereby providing a second transmission contingency source of service for that distribution facility.  If one transmission circuit is out-of-service, the other transmission circuit will have sufficient capacity to serve the load of the Clay Substation.  This will allow the more limited load of the Jennersville PDM to be handled, if necessary, either through the Clay Substation or the 34 kV-system.  In addition, the transmission changes being made in this project can, if additional load necessitates it in the future, be used to create a second source of service to the Jennersville PDM. 


PECO states that the general line modification needed for this project is to create a second transmission circuit along the same transmission right-of-way that currently holds the Clay Tap.  This will convert the existing radial tap into an electrical "loop" that provides two sources of transmission service to the Clay Substation.  The existing Clay Tap is constructed on 36 lattice towers, nominally 86 feet in height but ranging from 75 to 102 feet.  PECO will reconfigure the existing circuit and install a second circuit by installing 36 to 38 new monopoles, with heights from approximately 111-146 feet, depending upon local topography.  These monopoles will be installed directly next to the existing lattice towers.  The existing transmission circuit will be transferred from the lattice towers to the monopoles, and a new, second transmission circuit will be installed on the new monopole structures.  PECO does not expect that installation of the monopole structures will require additional tree removals.  Once the monopoles are installed and the existing circuit has been transferred to the monopoles, the existing lattice towers will be deconstructed and removed.  All of this transmission line work will take place on an existing transmission line right-of-way, which has been used as a power line corridor for many years.  

PECO states that the design criteria used for the transmission line work described herein is set forth in the PECO's standards for transmission line construction. These design criteria meet or exceed the requirements of the National Electrical Safety Code ("NESC").  Furthermore, PECO will construct, operate and maintain the transmission facilities in a manner that satisfies or surpasses NESC standards.  The proposed project will not create an unreasonable risk of danger to the public health or safety. 


PECO states that the functional requirements of the project allow it to use existing rights-of-way and fee-owned or easement land for all of the modifications for this project.    In addition, and as explained earlier, this project involves reconfiguration of an existing transmission line by installing new monopoles directly next to the location of the existing lattice towers except directly next to Clay Substation, Jennersville PDM, and Doe Run switching station, where additional or differently-located structures may be necessary to electrically connect to the transformers or other electrical facilities.  This transmission line work will take place on an existing transmission line right-of-way, which has been used as a power line corridor for many years.  Before it performs construction work, PECO will conduct an analysis of the presence /absence of wetlands for the project.  Where wetlands are identified and access is required, they will be surveyed, marked in the field, and designated on drawings.  Where access over wetlands is necessary to perform the construction work, PECO will utilize temporary mats or other approved or permitted methods to avoid damage.  As a consequence of all of these factors, the transmission line modifications proposed for approval herein will create minimal new environmental and land use impacts. 


PECO states that the total cost for the transmission line work associated with the project is estimated to be $26,335,000.  This project has a needed in-service date of June 1, 2013 in order to be available to serve peak load in the summer of 2013.  In order to meet this in-service date, PECO needs to commence construction in May 2011. 

Upon review, the Commission finds that the PECO’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(i) and (v) because the line is being reconductored and reconstructed entirely on an existing transmission line right-of-way, and the size, character, design, or configuration, of the proposed HV line will not substantially alter the right-of-way of the existing HV line associated with the project.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting; THEREFORE,
IT IS ORDERED:


           
That the Letter of Notification filed by PECO Energy Company for the Doe Run-Jennersville-Clay 230 kV Transmission Line (the “Clay Tap”) located in Penn, New 
London, Upper Oxford and Franklin Townships, Chester County, PA, is hereby approved.

[image: image1.png]



   BY THE COMMISSION,


   Rosemary Chiavetta

   Secretary

(SEAL)

ORDER ADOPTED: February 10, 2011
ORDER ENTERED: February 10, 2011
PAGE  
7

