ATTACHMENT “1”

OTTER CREEK – CONASTONE 230 kV TRANSMISSION LINE REBUILD
NECESSITY STATEMENT

TABLE OF CONTENTS

	SECTION
	TOPIC
	PAGE

	
	
	

	A.
	INTRODUCTION……………………..……………………………......
	1

	
	
	

	B.
	OVERVIEW OF VINTAGE CONDUCTOR PROGRAM……..............
	1

	
	
	

	C.
	PROPOSED SOLUTION……………………………………….............
	5

	
	
	

	
	LIST OF TABLES
	

	
	
	

	TABLE 1
	VINTAGE CONDUCTOR PROGRAM……………………………......
	4

	
	
	

	TABLE 2
	PPL Electric Analysis of Rebuild vs Rehabilitate…..
	6

	
	
	


ATTACHMENT “1”

OTTER CREEK - CONASTONE 230 kV TRANSMISSION LINE REBUILD
NECESSITY STATEMENT

A.
INTRODUCTION

PPL Electric Utility Company (“PPL Electric”) is requesting approval from the Public Utility Commission (“Commission”) to rebuild the PPL Electric section of the Otter Creek – Conastone 230 kV Transmission Line.  This transmission line begins at the Otter Creek Switchyard located in Chanceford Township, York County, crosses through East Hopewell and Hopewell Townships, and crosses the Maryland border.  The portion of the line south of the southernmost structure in Pennsylvania is owned by Baltimore Gas and Electric (“BG&E”).  This proposed project is part of PPL Electric’s Vintage Conductor Program, which is described in detail below. The program was developed to address deteriorated facilities in PPL Electric’s transmission system.  The proposed project will be designed to accommodate a second 230 kV circuit.  The line will initially be constructed and operated for a single 230 kV circuit.  As explained in detail below, reconstruction of the transmission line is required to maintain system reliability.  

The estimated cost to design and rebuild the transmission line is $16,856,705.  Construction is scheduled to begin in July 2012 to support the in-service date of April 2013. 

A PPL Electric system map showing the existing transmission facilities with design voltages of 35 kV or greater is included in the Attachment “1” map pocket.  Although this Necessity Statement provides a broad discussion of the Vintage Conductor Program, this filing addresses only the portion of the Otter Creek – Conastone Transmission Line, which is located from the Otter Creek Switchyard to and including the southernmost structure in Pennsylvania.  

B.
OVERVIEW OF VINTAGE CONDUCTOR PROGRAM
As previously described in the Manor – Graceton 230 kV Line Replacement Letter of Notification (Docket # A-2011-2219913), the PPL Electric transmission system includes multiple 230 kV line segments that are approximately 80 years old.  These line segments were installed in the mid-1920s through the 1930s.  Lines that operate at 230 kV are part of the bulk electric system.  These lines serve as major pathways for the flow of large amounts of electrical power: (a) from one bulk substation or switchyard to other bulk substations within the electric utility’s territory, or (b) between one electric utility and another (tie line).  At bulk substations, power is transformed to lower voltage levels for delivery to residential, commercial, or industrial customers.  PPL Electric owns approximately 1,000 miles of transmission lines that operate at 230 kV.  The Otter Creek – Conastone Transmission Line connects the PPL Electric territory with the BGE territory in Maryland, and is one of multiple outlets for the generation facilities located along the lower Susquehanna River.

The Vintage Conductor Program began as a result of a review process of the 230 kV line located between the Bushkill 230 kV Switchyard and Wallenpaupack Hydroelectric Plant.  PPL Electric’s Transmission Engineering group informed the Transmission Planning group that the transmission line had deteriorated facilities.  The Transmission Engineering group subsequently identified other 230 kV lines dating to the same construction era with similarly designed structures and conductors.
  Those conversations between the Planning and Engineering groups resulted in the identification of eleven line segments that contained aged and deteriorated facilities.  Those segments, totaling approximately 140 miles, were grouped into a program that PPL Electric has referred to as the Vintage Conductor Program.  The process of identifying aged and deteriorated facilities is on-going.  Three more line segments have been identified for further analysis.  

In 1983, PPL Electric tested a portion of this “vintage conductor” – specifically those line segments located between the Wallenpaupack, Blooming Grove, Bushkill, and Siegfried electric stations.  At the time of this testing, the steel core of the 795 conductor was showing deterioration, but the greatest concern to PPL Electric personnel was the deterioration occurring at the conductor splices. 

Consequently, most splices in the line between Wallenpaupack and Siegfried stations were replaced.  Based upon Transmission Engineering determinations, the line conductor was expected to last another 10 to 15 years.  That time frame has been exceeded, and no follow up examination or similar major repair work has been performed on the other segments.  PPL Electric, however, has performed and continues to perform aerial inspections of these facilities on average every four years.  Specific maintenance tasks are identified from this inspection, and PPL Electric prioritizes, schedules, and completes these tasks in a timely manner. 

In early 2010, PPL Electric hired an outside engineering consultant
 to perform an independent field investigation and assessment of the line segments
.  

The engineering consultant reported on the degree of deterioration of the structural components, foundations, insulators, line hardware, shield wire, grounding, signage, paint, and galvanizing.  The state of right-of-way encroachment and adjacent land features were also reported.  

A short length of conductor (loop) and its insulator string used to connect two spans of conductors at tension towers was removed and examined (laboratory and visual) from four of the eleven line segments. Overhead line conductor was not examined or tested to determine its physical condition or its tensile strength.  Tensile strength testing would have required a line outage in order to physically remove multiple samples from the span (i.e.; conductor located between two adjacent towers) at numerous locations along the identified line segments.  Furthermore, an examination of the conductor would be an unnecessary initial step if the other tower-line components (i.e.; structures, foundations, etc) were found to be significantly deteriorated, as was expected from the findings in 1983.  Sampling of overhead conductor will only be initiated if deteriorated tower-line components can be remedied by rehabilitation.  The independent external engineering consultant, DiGioia Gray & Associates, identified a statistically significant number of structures for each line segment.  The identified structures, and associated foundations and line equipment were then inspected in the field by DiGioia Gray & Associates.  Results of the evaluations were summarized in line-specific assessment reports.    

Based upon the issues that were identified in 1983 and the recent findings of the independent external engineering consultant, the identified line segments are now at an increased risk of failing, thus creating a safety concern for both the public and PPL Electric field personnel.  Further, if this issue is left unresolved, the potential for degradation in grid reliability will exist due to an increased risk to line equipment outages.  PPL Electric determined that a program to systematically upgrade these line segments was required, and established the Vintage Conductor Program to perform the necessary upgrades.

The original nine segments included in the Vintage Conductor Program, which total approximately 90 miles, and the two projects that are included in the Susquehanna-Roseland 500 kV project are identified in Table 1.  Review of PPL Electric’s transmission system to determine whether additional segments need to be replaced is on-going. 

TABLE 1

Vintage Conductor Program

	Super Project No.
	Project Name / Line Segment
	Line Segment Miles
	Original 
In-Service Date

	9056
	Manor - Graceton 
	14.52
	1937

	9057
	Otter Creek – Conastone
	11.98
	1933

	9054
	Martins Creek – Siegfried # 2
	10.69
	1926

	9049
	Hosensack – Wescosville # 3
	9.76
	1928

	9053
	Whitpain – Buxmont
	7.72
	1928

	9050
	Shawnee – Bushkill
	2.20
	1926

	9051
	Fox Hill – Shawnee
	8.27
	1926

	9052
	Martins Creek – Monroe
	16.14
	1926

	9055
	Hummelstown – Middletown Junction # 1
	7.00
	1954

	N/A
	Bushkill – Blooming Grove (note 1)
	21.80
	1926

	N/A
	Blooming Grove – Wallenpaupack (note 1)
	29.40
	1926


N/A – not applicable.

(note 1) – Line segments to be upgraded as part of the Susquehanna-Roseland 500 kV Line project. 
C.
PROPOSED SOLUTION

Permanent removal of the Otter Creek – Conastone 230 kV line from service would weaken the 230 kV system in southern Pennsylvania.  When the line is temporarily removed from service to perform line maintenance, an unplanned outage of any nearby 230 kV line would cause the remaining lines in the Manor, Otter Creek, and Brunner Island area to become overloaded.  Abandonment of the Otter Creek - Conastone line is, therefore, not an option.   

Technical solutions to restore the deteriorated components of the line segments, as identified in the “Vintage Conductor Recommendations,” would be to either:


(a) rehabilitate the components (i.e.; structures, foundations, conductor, insulators, and line hardware), or

(b) completely rebuild the line segments.

PPL Electric, in making its determination, took into consideration the following statement about the Otter Creek – Conastone Line from the 2010 Condition Assessment Reports from DiGioia Gray & Associates:

“Given that six of twelve structures inspected have severe foundation conditions, we do not advise that this line be rehabilitated.  Repairing the majority of structures for severe section loss at the base plate and at ground line is not economically feasible and would result in a reliability index significantly lower than a newly constructed transmission line.”

PPL Electric also prepared a cost analysis and determined that a complete rebuild of the Otter Creek – Conastone Transmission Line was less expensive than rehabilitation.  Specifically, the PPL Electric cost analysis summarized in Table 2 concluded that rehabilitation costs would be 1.01 percent greater than the total rebuild cost for the Otter Creek – Conastone Transmission Line. 

TABLE 2

PPL Electric Cost Analysis of Rebuild vs. Rehabilitation

	
	Labor & Material Cost


	Ratio of Costs; Rehabilitation to Rebuild 

	Scope
	Rebuild
	Rehabilitation 
	

	
	
	
	

	Labor and materials related to structures, foundations, insulators, line hardware and paint.
	$9,048,180
	$9,277,067
	1.03

	Common elements (includes labor and materials related to conductor, design and engineering, project management, acquisition of additional right-of-way, permitting, siting, PUC certification, environmental, and general overhead costs).
	$7,808,525
	$7,808,525
	1.00

	Total
	$16,856,705
	$17,085,592
	1.01


In addition, Burns & McDonnell (“B&McD”), a consulting engineering firm, prepared an independent cost evaluation on an individual line segment basis and compared rehabilitation of conductor, structures, foundations, and associated line equipment against a complete rebuild.  The results of the B&McD evaluation for the Otter Creek – Conastone line were consistent with the PPL Electric cost evaluation.  

To further support the decision to completely rebuild rather than rehabilitate the Otter Creek – Conastone Transmission Line, PPL Electric also considered the following additional issues that are more efficiently addressed by rebuilding:

· Bent or missing steel components on the existing towers would require removal and/or replacement, or the installation of additional bracing, to correct the structual deficiencies.  Depending on the number of crews assigned to the project, that work will either be one tower at a time, or multiple towers grouped together for the repair work.  On the other hand, the rebuild option will require only the erection of a single mono-pole structure after a new single concrete foundation has been poured and cured.  

· All insulator sets at the top of each tower should be replaced because of their age, the condition of the insulating material within the insulator, and the heavy contamination with pollutants from long-term exposure.

· Line hardware and related attachment steel on each tower should be removed and replaced, because of the wear on the material at the connecting points.  Metal against metal degradation was observed during the field inspections.

· Splices in the conductor should be replaced, due to their age, outdated design, and early manufacturing processes that were used to make the devices in the 1920s and 1930s.

· Conductors should be replaced based on their age.

· Grounding at each structure or tower leg must be upgraded by adding counterpoise in order to meet current safety standards.

· The overhead shield wires require replacement due to age, condition, and possible repositioning in order to bring the tower-line structure up to current lightning standards.  In its assessment reports, the independent external engineering consultant noted that some line segments do not have the appropriate shielding angle, which makes the tower-line more susceptible to lightning strikes.

PPL Electric will experience technical, safety, and environmental benefits that would not exist if the rehabilitation option were chosen.  Those benefits are discussed in more detail below.  In addition, completely rebuilding the Otter Creek – Conastone line is less expensive for PPL Electric than attempting to rehabilitate the line.  

Rebuilding the Otter Creek – Conastone Transmission Line will result in new structures that are capable of supporting an initial single-circuit line that would meet current National Electrical Safety Code (“NESC”) standards with regard to mechanical loading, including improved ground clearances.  The new structures will have an expected life that will exceed that of reconditioned structures.  

Using new structures in the rebuild will allow for the future installation of a second circuit, ultimately providing a double-circuit capability on the same right-of-way footprint that the existing “vintage conductor” now occupies.  Designing for two circuits on the same transmission line maximizes the use of the right-of-way and minimizes the impact of the rebuilt tower-line on the environment now and in the future.  This is the most economical and environmentally friendly method to allow for future expansion of the transmission system.  Planning now for a future double-circuit line eliminates the need for new rights-of-way at a future date, and minimizes future tree clearing for a second circuit.  The new structures will enable PPL Electric to comply with its modern magnetic field policy, and will improve the magnetic field values within and at the edge of the right-of-way.  Future double-circuit design also has the potential to employ “reverse phasing,” which would further reduce the electromagnetic field levels.  The identified line segments (Table 1) now exist as single-circuit designs, and have no capability to be converted to future double-circuit operations unless they are rebuilt.

Furthermore, each new single circuit line will be designed to use 1590 kcmil ACSR conductor instead of the existing 795 conductor.  As stated in the PPL Electric “Reliability Principles and Practices” (“RP&P”) document, the larger conductor is standard for new 230 kV line construction.  The 1590 kcmil ACSR conductor will provide an ampacity of 653 MVA summer normal, instead of the 425 MVA ampacity of the deteriorated line.  While line loadings on these deteriorated segments are not the single driving reason for the Vintage Conductor Program, as the regional loads on the 230 kV electrical network grow over time, the rebuilt Otter Creek – Conastone line will have the capacity to support greater electrical loads because of the proposed upgrade.

The larger conductor also will reduce system losses and may reduce system constraint on power flows.

The existing structures are not capable of supporting 1590 kcmil ACSR without additional reinforcement.  Using a smaller conductor, such as is currently on the tower-line, would not be the best technical or most economical solution, and would not meet current PPL Electric design practices.  It would also make the Otter Creek – Conastone line less capable of supporting future load growth in that line corridor.

Rehabilitation of the Otter Creek – Conastone Transmission Line will require longer construction periods to perform the numerous repairs on a tower-by-tower basis.  Most of the structures on the Otter Creek – Conastone Transmission Line have four foundations, because of the use of steel lattice towers.  Where major foundation repairs are required, the individual tower will require temporary structural support while each foundation is replaced.  Two or more towers likely would be grouped together for foundation repair work.  A period of weeks will need to pass as the old concrete is removed and new concrete is placed and cured prior to placing the mechanical load back onto the new foundations.  Foundation replacement would impede the speed at which crews could move from one structure and its associated foundations to the next.  The process of repairing the foundations would prolong the construction period significantly if PPL Electric had to rehabilitate the existing line.  

PPL Electric’s current practice in rebuilding or reconductoring of lines is to install optical ground wire (“OPGW”) instead of steel ground wire.  Non-conductive strands of optical fiber material are surrounded by one or more layers of steel and/or aluminum wire to create the OPGW.  This design change is employed so that protective relay schemes do not depend on less reliable hard-wired telephone circuits, or on power line carrier equipment that uses the line conductors for the communication path.  The OPGW provides a relaying and communication path with improved reliability. 

The completion date for each specific Vintage Conductor Program will be coordinated with the timing of the overall Asset Optimization Strategy (AOS) program, which is scheduled to conclude by 2020.  Because of the physical condition of the Otter Creek – Conastone line segment, its in-service date has been established as April 2013. 
� 795 thousand circular mils (“kcmil”), aluminum conductor steel reinforced (“ACSR”), 54/7 stranding, and variations of that stranding (“795 Conductor”).


� DiGioia Gray & Associates; Monroeville, PA 15146


� Two of the line sections, specifically the Bushkill – Blooming Grove and Blooming Grove – Wallenpaupack line segments, were excluded from the field investigation performed by the engineering consultant because those segments are to be completely rebuilt as part of the proposed Susquehanna – Roseland 500 kV line project.  A recent Commission decision approved the Susquehanna – Roseland project and associated rebuilding of these two line segments.  Appeals from that decision are pending.









i
ATTACHMENT “1” – NECESSITY STATEMENT

