PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held June 30, 2011

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Jr., Vice Chairman
      Tyrone J. Christy
Wayne E. Gardner 

James H. Cawley
Letter of Notification of PPL Electric 

Utilities Corporation, filed pursuant to 

52 Pa. Code Chapter 57.72, with respect 




A-2011-2237445
to the Modification of the Lakeville
138/69 kV Tap Line in Paupack Township,

Wayne County, PA.

ORDER

BY THE COMMISSION:

On April 21, 2011, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

(iii) An HV line which is proposed to be located entirely within a public road.

(iv) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(v) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi) An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vii) An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Wayne County Commissioners, Wayne County Planning Commission, Paupack Township Board of Supervisors, Paupack Township Planning Commission, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PPL Electric seeks Commission approval for the siting and construction of the modification to the Lakeville 138/69 kV Tap Line (“the Project”), which will consist of approximately 70 feet of new 138/69 kV transmission line to be constructed in Paupack Township, Wayne County, Pennsylvania. 
PPL Electric proposes to construct a short tap line adjacent to its existing Lakeville 69-12 kV Substation.  PPL Electric states that it requires the new tap line to serve customers using a mobile substation that will allow the Company to perform routine maintenance without disrupting service to its customers, and restore service during an unplanned outage of the substation.  The Project which will be approximately 70 feet in length requires the replacement of one wood pole and the addition of one pole.  Both new poles will be steel monopoles, approximately 79 feet tall, and will be direct-embedded and guyed.  The Tap Line will be designed and constructed for 138 kV operation but will initially operate at 69 kV.



PPL Electric states that the Project is located on PPL Electric's Lakeville Substation property near the intersection of Purdytown Pike (PA 590) and Daniels Road, in Paupack Township, Wayne County.  The area surrounding the substation is generally wooded to the north and south, and agricultural to the east and west, with a few scattered homes in the area.  PPL Electric anticipates that the incremental visual impacts of the Project will be minimal due to the remoteness of the area and the small size of the Project. 

PPL Electric states that the proposed modification of the Lakeville 138/69 kV Tap Line will consist of three power conductors and one overhead ground wire.  The power conductors will be 556.5 kcmil (thousands of circular mils)
 24/7 strand ACSR
.  The overhead ground wire will be 3/8- inch steel and will provide lightning protection for the proposed Tap Line.
The Project will not create any unreasonable risk of danger to the public health or safety.  It will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable NESC minimum standards and all applicable legal requirements.

PPL Electric states that the Project will be constructed entirely on property owned in fee by PPL Electric. No additional rights-of-way are required. 
PPL Electric states that communication towers, pipelines, or other utilities will not be affected by the proposed Lakeville 138/69 kV Tap Line Modification. The nearest airport is approximately 2.4 miles from the project area.  


The Project was reviewed with representatives of Paupack Township and Wayne County, and neither the Township nor the County has any objection. 



PPL Electric states that the estimated cost of the transmission line modifications described above is $110,600.  Construction is scheduled to begin as soon as possible in order to meet a November 2011 in-service date.  This in-service date is required in order to avoid outages during upcoming scheduled maintenance. 
Upon review, the Commission finds that the PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the length of the project is less than two miles.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting.  We note that our approval of the Letter of Notification does not reach the issues of accounting treatment and cost recovery; THEREFORE,

IT IS ORDERED:




That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the modification of the Lakeville 138/69 kV Tap Line in Paupack Township, Wayne County, PA, is hereby approved.

[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

(SEAL) 

ORDER ADOPTED: June 30, 2011
ORDER ENTERED: July 1, 2011
� A circular mil is the cross-sectional area of a wire one mil in diameter, where 1 kcmil == 0.5067 mm2


2 Aluminum conductor steel reinforced.








PAGE  
5

