PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held July 14, 2011

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Jr., Vice Chairman

Wayne E. Gardner 

James H. Cawley 
Pamela A. Witmer,
Letter of Notification of PPL Electric 

Utilities Corporation, filed pursuant to 

52 Pa. Code Chapter 57.72, with respect 




A-2011-2237488
to the Allentown-Siegfried #1 & #2 138 kV 

Transmission Line and the East Allentown 

#1 & #2 138 kV Tap Line in the City of 

Allentown, Lehigh County, Pennsylvania. 

ORDER

BY THE COMMISSION:

On April 21, 2011, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(v) and (vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

(iii) An HV line which is proposed to be located entirely within a public road.

(iv) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(v) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi) An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vii) An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Lehigh County Commissioners, Lehigh Valley Planning Commission, City of Allentown, City of Allentown City Council, City of Allentown Planning Commission, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PPL Electric seeks Commission approval for the reconstruction of the Allentown-Siegfried #1 & #2 138 kV Transmission Line, and the East Allentown #1 & #2 138 kV Tap Line, located in the City of Allentown, Lehigh County, Pennsylvania.
The purpose of the proposed reconstruction is to raise the lines to meet PPL Electric's clearance requirements so that the Pennsylvania Department of Transportation ("PennDOT") can proceed with its planned American Parkway Extension Project.
PPL Electric states that PennDOT plans on constructing the American Parkway Extension Project.  A portion of this Project includes building a bridge over the Lehigh River, in order to connect the portions of American Parkway that run on either side of the river, as well as the associated ramps and intersections.  In order for PennDOT to make its planned upgrades, it has requested that PPL Electric raise the Allentown - Siegfried #1 & #2 138 kV Transmission Line and the East Allentown #1 & #2 138 kV Tap Line.
PPL Electric states that the proposed reconstruction of the Allentown - Siegfried #1 & #2 138 kV Transmission Line and the East Allentown #1 & #2 138 kV Tap Line will take place on the centerline of the existing rights-of-way, in the City of Allentown, Lehigh County, Pennsylvania.  PPL Electric anticipates that the incremental visual impacts of the Project will be minimal because the reconstruction will take place entirely within the currently maintained rights-of-way.

Further, the proposed reconstruction of the Allentown - Siegfried #1 & #2 138 kV Transmission Line and the East Allentown #1 & #2 138 kV Tap Line will involve the reconstruction of approximately 680 feet of the Allentown - Siegfried # I & #2 13 8 k V and approximately 1220 feet of the East Allentown #1 & #2138 kV Tap Line.  The rebuilt sections of the two lines will be constructed along the present centerlines of the existing rights-of-way.  No additional right-of-way is required for this Project.  The proposed relocation will not change the functionality of the transmission system.
PPL Electric states that the proposed reconstruction of the Allentown - Siegfried #1 & #2 138 kV Transmission Line will require the removal of four existing transmission poles, to be replaced by two new transmission poles.  The existing poles, which are approximately 85 feet in height, will be replaced with new poles that are approximately 120 feet in height.  The average span of the existing poles is approximately 200 feet.  After reconstruction, there will be a single span that will be approximately 680 feet in length.  The existing conductors and overhead ground wire on this section of the line will be replaced.  The power conductors will be 556.5 kcmil (thousands of circular mils)
 24/7 strand ACSR.
  The overhead ground wire will be 3/8-inch steel and will provide lightning protection for the reconstructed Transmission Line. 
Also, the proposed reconstruction of the East Allentown #1 & #2138 kV Tap Line will require the removal of six existing transmission poles, to be replaced by three new transmission poles.  The existing poles, which are approximately 80 feet in height, will be replaced with new poles that are approximately 95 feet in height.  The average span of the existing poles is approximately 220 feet.  After reconstruction, the spans will average approximately 610 feet in length.  The existing conductors and overhead ground wire in this section of the East Allentown #1 & #2 138 kV Tap Line will be replaced.  There will be three power conductors and one overhead ground wire. The power conductors will be 556.5 kcmil 24/7 strand ACSR.  The overhead ground wire will be 3/8-inch steel and will provide lightning protection for the reconstructed Tap Line.
PPL Electric states that the proposed reconstruction of the Allentown - Siegfried #1 & #2 138 kV Transmission Line and the East Allentown #1 & #2 138 kV Tap Line will not create any unreasonable risk of danger to the public health or safety.  The proposed reconstructed line sections will be designed, reconstructed, operated, and maintained in a manner that meets or surpasses all applicable NESC minimum standards and all applicable legal requirements.  
PPL Electric states that communication towers, pipelines, or other utilities will not be affected by the proposed reconstruction of the Allentown - Siegfried #1 & #2 138 kV Transmission Line and the East Allentown #1 & #2 138/69 kV Tap Line.  Lehigh Valley Airport is the nearest airport and is located approximately 1.5 miles to the north of the Project site.  PPL Electric will contact the PennDOT Bureau of Aviation and the Federal Aviation Administration to ensure that the proposed reconstruction will not be a hazard to flight operations.


The Project was reviewed with representatives of the City of Allentown and Lehigh County, and neither the City nor the County has any objection. 



PPL Electric states that the estimated cost to reconstruct these lines is $850,000 and will be borne entirely by PennDOT. The Project has a required in-service date of April 2012.  Construction is scheduled to begin by January 2012 in order to meet the in-service date. 
Upon review, the Commission finds that the PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(v) and (vi) because the reconstruction will take place entirely within existing rights-of-way, will not substantially alter the rights-of-way and the Project is less than two miles in length.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting.  We note that our approval of the Letter of Notification does not reach the issues of accounting treatment and cost recovery; THEREFORE,

IT IS ORDERED:




That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the reconstruction of Allentown - Siegfried #1 & #2 138 kV Transmission Line and the East Allentown #1 & #2 138/69 kV Tap Line in the City of Allentown, Lehigh County, PA is hereby approved.

[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

(SEAL) 
ORDER ADOPTED: July 14, 2011
ORDER ENTERED: July 18, 2011
� A circular mil is the cross-sectional area of a wire one mil in diameter, where 1 kcmil = 0.5067 mm 2.


� Aluminum conductor steel reinforced.





PAGE  
6

