PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held August 25, 2011

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Vice Chairman
      Wayne E. Gardner 

James H. Cawley 
Pamela A. Witmer,
Letter of Notification of PPL Electric 

Utilities Corporation, filed pursuant to 

52 Pa. Code Chapter 57.72, for approval                                         A-2011-2237599

of the reconstruction of the Hosensack-

Wescoville 230 kV Transmission Line 
in Upper Macungie, Lower Macungie, 

Upper Milford and Lower Milford
Townships, Lehigh County, Pennsylvania.
ORDER

BY THE COMMISSION:

On April 25, 2011, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(i) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

(iii) An HV line which is proposed to be located entirely within a public road.

(iv) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(v) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi) An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vii) An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Sections 57.72(d)(3), 57.74 (b)(c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Upper Macungie Township Board of Supervisors, Lower Macungie Township Manager, Lower Milford Township Manager,  Upper Milford Township Manager, Lehigh Valley Planning Commission, Lehigh County Commissioners, Lehigh County, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PPL Electric seeks Commission approval to reconstruct approximately 8.7-mile portion of the eighty three year old Hosensack - Wescosville # 3 230 kV Transmission Line ("Hosensack - Wescosville #3 Line").  The proposed reconstruction involves a section of the transmission line which begins near the Hosensack Substation, located in Lower Milford Township, Lehigh County, and traverses portions of Upper Milford, and Lower Macungie Townships in Lehigh County, and ending at the Wescosville Substation in Upper Macungie, Lehigh County, Pennsylvania.


PPL Electric states that it proposes to minimize impacts of the Hosensack - Wescosville # 3 Line by rebuilding it along its existing route and in the existing right-of-way. The existing right-of-way is sufficient to accommodate the rebuilt line and, in order to reduce the possibility of vegetation-related outages, has already been cleared of vegetation that could interfere with the operation of a high voltage transmission line. 



PPL Electric states that this project is part of PPL Electric’s Vintage Conductor Program, which was developed to address aged, deteriorated facilities in PPL Electric’s transmission system.   Under the Vintage Conductor program, PPL Electric has identified old and/or deteriorated transmission lines that require reinforcement in order for PPL Electric to continue to provide safe and reliable service to its customers.  Most of the transmission lines in the program were originally constructed in the 1920s and 1930s. 



Presently, the structures for the Hosensack-Wescosville # 3 Line are steel lattice towers.  A detailed inspection of the structures has revealed that the concrete foundations are in poor condition and many would need to be replaced.  Further, many steel members of the lattice structures are either bent or missing, which severely weakens the structure.  The insulators, conductors and lightning protection all have been exposed to the elements and will not continue to provide dependable service unless they are replaced. 



PPL Electric states that this line is needed in order for PPL Electric to provide reliable service to customers.  The Hosensack-Wescosville #3 Line is the only 230 kV source of electric power to the 230-69 kV transformer # 2 at Wescosville.  Permanent removal of the Hosensack​-Wescosville #3 Line from service would weaken the 230 kV-system in eastern Pennsylvania.  When this line is temporarily removed from service to perform line maintenance during heavy load periods, an unplanned outage of either the Wescosville 138-69 kV transformer # 1, or # 4 causes an overload on the remaining transformer.  The Hosensack -Wescosville #3 Line and the 230-69 kV transformer # 2 at Wescosville would normally relieve this overload condition.  In addition, the 230-69 kV transformer # 2 is used to relieve an overload on the Wescosville 500- 138 kV transformer # 3 during peak load periods under specific generation dispatches or abnormal sectionalizing.  Therefore, abandonment of the Hosensack-Wescosville #3 230 kV Transmission Line is not an option. 

According to PPL Electric, the proposed reconstruction of the Hosensack - Wescosville # 3 Line will involve the removal of the existing transmission line, including the steel lattice towers and conductors, all of which were built in the late 1920’s.  The existing single circuit 230 kV transmission line is supported by lattice towers with an average height of approximately 90 feet and average span of approximately 1,100 feet.  The proposed rebuilt transmission line will be designed to accommodate a single circuit 230 kV line.  The proposed new transmission line will consist mostly of single-shaft steel poles equipped with upswept steel arms.  Angle structures may consist of single, two- or three-pole structures depending on the severity of the angle.  All poles will be installed on concrete foundations.  Additionally, some angle structures may be guyed.  Altogether, this project requires the installation of approximately 42 structures with an average height of 120 feet. The average span length will be 1,100 feet.  Three power conductors and one optical ground wire (“OPGW”) will be installed.  The power conductors will be 795 kcmil
 (thousands of circular mils) 30/19 stranding ACSR.
  The OPGW will be 0.752-inch diameter OPGW with 48 single mode fibers.  In addition, a second overhead shield wire will be installed which will consist of ½-inch extra high-strength steel. 

The rebuilt sections of the two lines will be constructed along the present centerlines of the existing rights-of-way.  No additional right-of-way is required for this Project.  The proposed relocation will not change the functionality of the transmission system.
PPL Electric states that the proposed reconstruction of the Hosensack - Wescosville # 3 Line will not create any unreasonable risk of danger to the public health or safety.  The proposed reconstructed line sections will be designed, reconstructed, operated, and maintained in a manner that meets or surpasses all applicable NESC minimum standards and all applicable legal requirements.  
PPL Electric states that no communication towers, pipelines, or other utilities will be affected by the proposed Hosensack -Wescosville # 3 Line.  Queen City Airport is the nearest airport and is located 3.2 miles east of the rebuilt line.  


According to PPL Electric, the proposed Hosensack - Wescosville # 3 Line was reviewed with representatives of the Lower Milford, Upper Milford, Lower Macungie, and Upper Macungie Townships and Lehigh County, and neither the townships nor the County has any objection to the project. 



PPL Electric states that the estimated cost to reconstruct the Hosensack - Wescosville # 3 Line is $12,500,000.  Construction is scheduled to begin in fall of 2012 in order to meet an in-service date of November 2013.

Upon review, the Commission finds that PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(i) because the reconstruction will take place entirely within existing rights-of-way, and will not substantially alter the rights-of-way.  Moreover, the Commission has reviewed the filing and finds it to be consistent with the applicable law and Commission policy regarding transmission line siting.  We note that our approval of the Letter of Notification does not reach to the issues of accounting treatment and cost recovery; THEREFORE,

IT IS ORDERED:



1.
That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the reconstruction of the Hosensack-Wescosville 230 kV Transmission Line in Upper Macungie, Lower Macungie, Upper Milford and Lower Milford Townships, Lehigh County, PA is hereby approved.

           2.
That this proceeding at Docket No. A-2011-2237599 be closed.

[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

(SEAL) 
ORDER ADOPTED: August 25, 2011
ORDER ENTERED: August 25, 2011
� A circular mil is the cross-sectional area of a wire one mil in diameter, where 1 kcmil = 0.5067 mm 2.


� Aluminum conductor steel reinforced.


� PPL has indicated that PJM Interconnection has approved an outage for the line for the period Oct. 15, 2012 through April 29, 2013, and that their intent is to have the construction completed by the end of April 2013.





PAGE  
6

