PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held August 25, 2011

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Vice Chairman
      Wayne E. Gardner 

James H. Cawley 
Pamela A. Witmer,
Letter of Notification of PPL Electric 

Utilities Corporation, filed pursuant to 

52 Pa. Code Chapter 57.72, for approval                                         A-2011-2244371
To site and construct the Tafton #2 138/69
kV Tap Line in Blooming Grove Township,
Pike County, Pennsylvania. 
ORDER

BY THE COMMISSION:

On May 27, 2011, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

(iii) An HV line which is proposed to be located entirely within a public road.

(iv) An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(v) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi) An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vii) An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Sections 57.72(d)(3), 57.74 (b)(c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Pike County Commissioners, Pike County Planning Commission, Blooming Grove Township Board of Supervisors, Blooming Grove Township Planning Board, and other interested parties as listed in the Certificate of Service.  No protests were filed.  No hearings were held.



PPL Electric seeks Commission approval to site and construct the Tafton #2 138/69 kV Tap Line.  This proposed tap will be connected to the Tafton 138/69 kV Tap which serves the Tafton 69-12 kV substation to create a double tap-single feed (DT/SF) configuration that will provide a second source of electricity to the Tafton Substation and improve the reliability of electric service to customers in the area.   The project is located in Blooming Grove Township, Pike County.  

 

PPL Electric states that the project is required to transfer the electric supply source for the Tafton 69-12 kV Substation from the Blooming Grove – West Damascus 138/69 kV Transmission Line to the Blooming Grove – Honesdale 138/69 kV Transmission Line.  Presently, the Tafton Substation is served via a single circuit 138/69 kV tap off the Blooming Grove – West Damascus 138/69 kV Transmission Line.  The proposed project includes the construction of a second tap to the Tafton 69-12 kV Substation.  The new tap will be from the Blooming Grove – Honesdale 138/69 kV Transmission Line.  The DT/SF connection will be used by the Transmission Operations group to balance the load on the Blooming Grove- West Damascus line by transferring the load between the Blooming Grove-Honesdale line and the Blooming Grove- West Damascus line.  The DT/SF connection will also provide the Transmission Operations group the ability to transfer the Tafton load between the Blooming Grove-West Damascus Line and Blooming Grove-Honesdale Line for maintenance and during outages.


PPL Electric states that the new tap line will be designed and constructed for single-circuit 138 kV operation, although it initially will be operated at 69 kV.  The remaining portion of the tap, which was constructed in 1975, and pre-dated the siting regulations, presently operates at 69 kV but was designed and built for 138 KV-operation.  The modified tap will be operated at 138 kV when future load increases make it appropriate to do so.


According to PPL Electric, the proposed tap line design includes approximately 460 feet of new conductor which will be supported by 3 steel mono-poles, a steel double H-Frame structure and 2 Load Sectionalizing Air Break Switch (LSAB) structures.  One existing pole currently supporting the existing tap will be removed and the conductor will be re-hung on half of the new steel pole double H-Frame structure.  A pole previously installed during the construction of the Blooming Grove- Honesdale Line will be used for the proposed tap.  This structure, which is approximately 49 feet high, will be re-configured to accommodate the new tap and will be guyed.  The double H-Frame structure will be approximately 38 feet tall with conductors at 28 feet above grade and will be guyed.  The two LSAB structures will be approximately 57 feet tall and will be direct embedded.  A dead end pole will be placed at the northern end of the new tap line and will be approximately 57 feet tall and will be direct embedded.  Further, the new circuit will consist of three power conductors and one overhead ground wire.  The power conductors will be 556.5 kcmil
 (thousands of circular mils) 24/7 strand ACSR.
  A 3/8-inch steel overhead ground wire will provide lightning protection for the tap line.


 The new tap line will be constructed entirely within an existing transmission corridor partially situated on land owned in fee by PPL Electric and partially on existing right-of-way.  No additional right-of-way is required for the construction of the proposed tap.  
PPL Electric states that the proposed construction of the Tafton # 2 Tap Line will not create any unreasonable risk of danger to the public health or safety.  The proposed tap line will be designed, reconstructed, operated, and maintained in a manner that meets or surpasses all applicable National Electrical Safety Code (NESC) minimum standards and all applicable legal requirements.  
PPL Electric states that no communication towers, pipelines, or other utilities will be affected by the proposed Tafton # 2 Tap Line.  Mountain Bay Airpark, a private airport, is located approximately 4.1 miles west of the project site.  


According to PPL Electric, the proposed Tafton # 2 138/69 kV Tap Line was reviewed with representatives of the Blooming Grove Township and Pike County, and neither the township nor the county has any objection to the project. 



PPL Electric states that the estimated cost to construct the Tafton # 2 Tap Line is $565,000.  Construction is scheduled to begin in February of 2012 in order to meet an in-service date of September 2012.
Upon review, the Commission finds that PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) as the length of the tap line to be constructed is less than two miles.  Moreover, the Commission has reviewed the filing and finds it to be consistent with the applicable law and Commission policy regarding transmission line siting.  We note that our approval of the Letter of Notification does not reach to the issues of accounting treatment and cost recovery; THEREFORE,

IT IS ORDERED:



1.
That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the construction of the Tafton #2 138/69 kV Tap Line in Blooming Grove Township, Pike County, PA is hereby approved.

           2. 
That this proceeding at docket No. A-2011-2244371 be closed.

[image: image1.png]


BY THE COMMISSION,


   






Rosemary Chiavetta

   






Secretary

(SEAL) 
ORDER ADOPTED: August 25, 2011
ORDER ENTERED: August 26, 2011
� A circular mil is the cross-sectional area of a wire one mil in diameter, where 1 kcmil = 0.5067 mm 2.


� Aluminum conductor steel reinforced.





PAGE  
6

