PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA 17105-3265


          Public Meeting held October 14, 2011
Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Jr., Vice Chairman

      Wayne E. Gardner


James H. Cawley – Absent 
      Pamela A. Witmer
Letter of Notification of PPL Electric 

Utilities Corporation filed pursuant to 52 
Pa. Code Chapter 57 for approval of the                   


A-2011-2228595

reconstruction of the Pennsylvania portion

of the Otter Creek-Conastone 230 kV
transmission line in Chanceford, East

Hopewell and Hopewell Townships in 
York County, Pennsylvania.

ORDER

BY THE COMMISSION:

On February 28, 2011, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(i) and (v) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

            (ii)      An HV line which is proposed to be located entirely within a public road.

(iii)  An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.
(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.  

(vi) An HV line having a proposed route of 2 miles or less.


Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the U.S. Army Corp of Engineers, U.S. Fish and Wildlife Service, PA Department of Conservation and Natural Resources, PA Game Commission, PA Fish and Boat Commission, PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, York County Board of Commissioners, York County Planning Commission, Metropolitan Edison Company and other interested parties as listed in the Certificate of Service, including township supervisors and planning commissions.  No protests were filed.  No hearings were held.


PPL Electric seeks the Commission’s approval for the proposed reconstruction of the Otter Creek-Conastone 230 kV transmission line in Chanceford, East Hopewell and Hopewell Townships in York County, Pennsylvania.



PPL Electric states that the project involves rebuilding the Pennsylvania portion of the Otter Creek-Conastone 230kV Transmission Line which runs from the Otter Creek switchyard in Chanceford Township, York County, and traverses portions of East Hopewell and Hopewell Townships in York County.  PPL Electric’s portion of this line stops at the Pennsylvania-Maryland border.    


Under PPL Electric’s Vintage Conductor Program, old and/or deteriorated transmission lines, constructed mainly in the 1920s and 1930s, that are vital to providing safe and reliable customer service, are identified.  The Otter Creek-Conastone Line reconstruction will be the second such project in this program, the first is the Manor-Graceton Line reconstruction, filed as an LON at Docket Number A-2011-2219913.  Since the Otter Creek-Conastone Line was built and placed in service in 1933 and is now 78 years old, PPL Electric proposes to rebuild, rather than rehabilitate, all of the Pennsylvania portion except the first three spans starting at the switchyard dead end structure to the three pole angle structure.  This section was rebuilt previously as part of Yorkanna-Otter Creek Project, docketed at A-110500F0325.  


PPL Electric performed detailed inspections of the steel lattice structures along the 12 miles of the line and determined the concrete foundations were deteriorated and in need of repair.  Additionally, many steel members were bent or missing.  Along with the structures and concrete foundations, the hardware, insulators, conductors and lighting protection all have been exposed to the elements and are not capable of continuing to provide dependable service in the future.  PPL Electric analyzed whether it would be more appropriate to rebuild or rehabilitate the line.  The results showed that rebuilding the line would be more cost effective than rehabilitating a 78 year old transmission line and structures.  


Rebuilding the line will include the replacement of the 85 feet high steel lattice structures with steel monopole structures, 145 feet high, with upswept steel arms designed to accept the existing 230 kV circuit, with a future option of adding a second circuit at relatively low cost with little environmental impacts when future load growth demands.  The average span between the 60 proposed steel monopole structures will be 1,000 feet.  Angle structures may be single or two or three-pole structures depending on the severity of the angle.  Additional poles may be added to some angle structures when a second circuit is added to the line.  New monopoles will be constructed on concrete foundations adjacent to the existing towers along the centerline of the right-of-way, while some locations may need to be adjusted slightly to reduce environmental impacts.  


The existing right-of-way is 150 feet wide and sufficient to accommodate and rebuild the line.  Vegetation has been cleared to reduce vegetation-related power outages and therefore the impacts to vegetation on the right-of-way will be minimized at the time of reconstruction.  The present steel lattice structures, which have a single circuit, will be removed from the right-of-way.  The new transmission line will consist of three 1590 KCMIL, 45/7 stranding ACSR power conductors.  Lightning protection will be provided by a .752 inch diameter optical ground wire with 48 single mode fibers.  A second circuit may be added when future load growth makes it appropriate to do so.  PPL Electric is advised that if it adds the second circuit, it must file a new Letter of Notification for the project.


PPL Electric states that the existing lattice structures are 57 ft wide and have a footprint of 900 square feet with four concrete footings per structure.  The new monopole structures will be 20 feet wide with the existing one circuit, or increase to 38 feet wide when a second circuit is added.  The footprint of the monopole will be approximately 64 square feet with a single foundation.     


PPL Electric states that the purpose of the project is to rebuild the existing Otter Creek-Conastone Line substantially in place.  The line is needed in order for PPL Electric to provide reliable service to customers.  When the line is temporarily out of service for maintenance, an unplanned outage of any nearby 230kV line would cause other lines in the Manor, Otter Creek and Brunner Island area to become overloaded, which could lead to failure of the overloaded lines and substantial outages affecting numerous customers for substantial periods until repairs are made.  Permanently removing Otter Creek-Conastone Line from service would cause service in the Chanceford, East Hopewell and Hopewell area to become unreliable and lead to substantial and prolonged service outages in the area.     


PPL Electric states that the rebuild of the Otter Creek-Conastone Line will have only minimal impacts on the natural and human environments.  The proposed line will cross 2.8 acres of wetlands and 23 streams.  Timber mats and other acceptable methods will be used during construction and on necessary access roads for wetland and stream crossings.  If any access roads must cross through wetlands, PPL Electric will obtain all required permits and comply with all conditions imposed on the issuance of such permits. 

Since the possibility exists that minimal tree clearing will be needed, PPL Electric states that Vegetation Management Specifications will be followed.  In areas with potentially affected rare, endangered or threatened plant species, PPL Electric will consult with the PA Department of Conservation and Natural Resources, (“DCNR”), to develop a specific vegetation management plan.  

PPL Electric has consulted with state and federal agencies to obtain information regarding endangered and threatened species in close proximity to Otter Creek-Conastone Line.  PPL Electric states that it will conduct all required surveys and resolve all potential conflicts with rare, endangered and threatened species prior to starting construction.   



PPL Electric states that the rebuild of the Otter Creek-Conastone Line will not cause any unreasonable risk to the health and safety of persons in its vicinity.  The line will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable National Electric Safety Code (“NESC”) minimum standards and all applicable legal requirements.  



Estimated cost to rebuild the approximate 12 mile transmission line with one circuit is $16,856,705.  Construction is proposed to commence on or around July 2012, with an in service date of April 2013, pending approvals.


The significant increase in the height of the poles has raised a critical concern in determining whether this Commission should process this filing as an LON or require filing as a full siting application
.  The Commission considered several issues in that regard, in addition to the change in height.  First, no party intervened to assert there was a substantial alteration of the right of way.  Second, the location of the poles is in the same proximity of the existing lattice structures.  No new poles will be placed on property where there were no existing poles, except for the angle structures where two or three poles may be needed.  Third, there will be a reduction in horizontal clearances.  The existing lattice structures, with a horizontal conductor configuration, have a much wider span at the conductors than the proposed monopoles, with vertical conductor configuration.  And fourth, there will be a reduction in the footprint of each pole on the right of way from the existing 900 square feet to 64 square feet.  





Upon review, the Commission finds that the PPL Electric Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(i) and (v) because it is to be reconstructed and the size, character, design and configuration of the proposed line does not substantially alter the right-of-way.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting.  We note that our approval of the Letter of Notification does not reach the issues of accounting treatment and cost recovery; THEREFORE,
IT IS ORDERED:



That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the Otter Creek-Conastone 230 kV Transmission Line in Chanceford, East Hopewell and Hopewell Townships in York County, PA, is hereby approved.

[image: image1.png]



BY THE COMMISSION,


Rosemary Chiavetta


Secretary

(SEAL)
ORDER ADOPTED: October 14, 2011
ORDER ENTERED:  October 17, 2011
� It is possible a change in the height alone could be a substantial alteration of the right-of-way depending upon the specific facts of a case.  





PAGE  
7

