# PENNSYLVANIA

# PUBLIC UTILITY COMMISSION

# Harrisburg, PA 17105-3265

# Public Meeting held April 26, 2012

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Vice Chairman

Wayne E. Gardner

# James H. Cawley

# Pamela A. Witmer

# Application Of PPL Electric Utilities

# Corporation, Filed Pursuant To 52 Pa.

# Code Chapter 57 Subchapter G, With			A-2012-2287565

# Respect To The West Shore-Harrisburg

# #1 & #2 138/69 kV Transmission Line

# In Lower Allen Township, Cumberland

# County, Pennsylvania.

# ORDER

BY THE COMMISSION:

On February 8, 2012, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to 52 Pa. Code §57.72(d)(1)(vi) of the Commission’s transmission line siting regulations.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

- An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

- An HV line which is proposed to be located entirely within a public road.

- An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Cumberland County Board of Commissioners, Cumberland County Planning Commission, Lower Allen Township Boards of Supervisors, Lower Allen Township Planning Commission and other interested parties as listed in the Certificate of Service.  No protest was filed and no hearing was held.

In this filing PPL Electric seeks Commission approval for the siting and construction of the West Shore-Harrisburg #1 and #2 138/69 kV Transmission Line (“West Shore-Harrisburg #1 and #2 Line”) to address reliability concerns in Lower Allen Township, Cumberland County, Pennsylvania.

PPL Electric states that the Project is required to resolve violations of PPL Electric’s Reliability Principles and Practices (“RP&P”) guidelines, and improve the reliability of service and operating flexibility of PPL Electric’s system in Lower Allen Township.  In addition the Project will help meet the increasing demand for electrical power in the area.

Further, PPL Electric states that the Project is required to alleviate a first contingency overload on the West Shore – Cumberland #1 69 kV Line that would result from the loss of the West Shore- Harrisburg #1 69 kV Line.  Presently, the White Hill 69-12 kV Substation is supplied by two tapped 69 kV lines, one from the West Shore-Cumberland #1 69 kV Line and the other from the West Shore-Harrisburg #1 69 kV Line.  In this configuration, the loss of the West Shore-Harrisburg #1 69 kV would cause all the White Hill Substation load to transfer to the West Shore-Cumberland #1 69 kV Line.  This scenario would create an overload on the West Shore-Cumberland #1 69 kV Line because its summer emergency rating is 124 MVA (“Megavolt Ampere’) and adding the total load of White Hill Substation would load the line to 127 MVA.  This is a violation of PPL Electric’s Non-Bulk Electric System RP&P regarding single contingency overloads.

According to PPL Electric, the proposed Project which will resolve the violation, involves the construction of a double-circuit, high-capacity 138/69 kV transmission line, approximately 1.3 miles long, between the West Shore 230-69 kV Substation and the present location of the White Hill Tap Lines.  At the tap point, the proposed line will be connected to the existing West Shore-Harrisburg #1 and #2 69 kV Lines.  Line arrangements will be completed so that the existing section of the West Shore-Harrisburg #1 Line between the West Shore Substation and the White Hill Tap point will be reconnected to the Cumberland #2 69 kV Line.  Also, the existing section of the West Shore-Harrisburg #2 Line between West Shore Substation and the White Hill Tap point will be reconnected to the White Hill #1 Tap Line establishing the new West Shore-White Hill #1 69 kV Tap Line.   Additional line rearrangements will be completed so that supply to the White Hill 69-12 kV Substation is directly from the West Shore 230-69 kV Substation.  Transferring the White Hill Substation load directly to the West Shore Substation reduces the loading on the West Shore-Cumberland #1 69 kV Line, thereby eliminating the first contingency overload condition.

PPL Electric states that the proposed West Shore- Harrisburg #1and #2 Line will utilize 29 single-shaft steel monopoles equipped with steel upswept conductor support arms.  An additional eight monopoles will be replacing existing structures to effect the rearrangement at the White Hill Tap point.  The average height of these monopoles is 85 feet.  Tangent structures will be direct embedded.  Angle structures will either be installed on concrete foundations or direct embedded and guyed.  The line will consist of six power conductors and one overhead ground wire.  The power conductors will be 556.5 kcmil, 24/7 stranding, ACSR (“Aluminum Conductor Steel Reinforced”) power conductors.  A 0.567 inch diameter Fiber Optic Overhead Ground Wire will be installed for lightning protection and for communication between circuit breakers.

PPL Electric states that the proposed construction of the West Shore-Harrisburg Line will not create any unreasonable risk of danger to public health or safety.  The proposed line sections will be designed, constructed, operated, and maintained in a manner that meets or exceeds all applicable National Electric Safety Code (“NESC”) minimum standards and all applicable legal requirements.

Further, PPL Electric states that it is anticipated that the proposed construction will have minimal incremental impacts on the area because the project will be located in close proximity to other PPL Electric transmission facilities.   The project will be located within existing rights-of-way.  PPL Electric does not need any additional right-of-way or other property interest in order to complete the project.  All work will be completed in existing rights-of-way or on land owned in fee by PPL Electric.

PPL Electric states that the project was reviewed with representatives of Lower Allen Township, as well as Cumberland County, Pennsylvania.  Neither the Township nor the County had any objection to the project.

The total estimated cost to design and construct the proposed project is $1,895,400, and will be paid by PPL Electric.  The construction is scheduled to commence in April 2012, to meet the scheduled in-service date of May 2013.

Upon review, the Commission finds that the PPL Electric’s Letter of Notification and manner in which it was filed conform to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the proposed line is to be constructed is less than two miles in length.  Above all, the Commission has reviewed the filing and finds it to be consistent with applicable law and Commission policy regarding transmission line siting, and therefore to be in the public interest.  We note that our approval of the Letter of Notification does not reach to the issues of accounting treatment and cost recovery; THEREFORE,

# IT IS ORDERED:

- That the Letter of Notification filed by PPL Electric Utilities Corporation with respect to the siting and construction of the West Shore-Harrisburg #1 & #2 138/69 kV Transmission Line in Lower Allen Township, Cumberland County, PA is hereby approved.

- That this proceeding at Docket No. A-2012-2287565 be closed.

BY THE COMMISSION,

# Rosemary Chiavetta

Secretary

(SEAL)

# ORDER ADOPTED: April 26, 2012

# ORDER ENTERED: April 26, 2012