# PENNSYLVANIA

# PUBLIC UTILITY COMMISSION

# Harrisburg, PA 17105-3265

# Public Meeting held February 14, 2013

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Jr., Vice Chairman

Wayne E. Gardner

# James H. Cawley

# Pamela A. Witmer

# Letter of Notification of PPL Electric

# Utilities Corporation, Filed Pursuant

# to 52 Pa. Code Chapter 57 Subchapter

# G with Respect to the Construction                                                      A-2012-2322734

# of the West Hershey #1and #2 138/69

# kV Transmission Tap Line in Derry

# Township, Dauphin County, Pennsylvania.

# Petition of PPL Electric Utilities Corporation

# for a Finding That a Building to Shelter

# Control Equipment at the West Hershey                                            P-2012-2322863

# 69-13 kV Substation to be Constructed

# in Derry Township, Dauphin County,

# Pennsylvania, is Reasonably Necessary

# for the Convenience or Welfare of the Public.

# ORDER

BY THE COMMISSION:

On August 30, 2012, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to Chapter 57, Subchapter G of the Commission’s regulations at 52 Pa. Code §57.72(d)(1)(vi), governing the siting and construction of high voltage transmission lines.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

(i)	An HV line which is proposed to be located entirely on an existing Transmission line right-of-way, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(ii)	An HV line which is proposed to be located entirely within a public road.

- An HV line which is proposed to be located entirely within applicant’s existing

transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- A line for which the voltage is proposed to be increased above its present

levels so long as the size, character, design, or configuration of the proposed

HV line does not substantially alter the right-of-way.

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi) An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Dauphin County Planning Commission, Dauphin County Board of Commissioners, Derry Township Planning Commission, Derry Township Board of Commissioners and other interested parties as listed in the Certificate of Service.  No protest was filed and no hearing was held.

PPL Electric proposes to construct the West Hershey #1 and #2 138/69 kV Transmission Tap Line (“West Hershey Tap Line”), which will extend approximately 150 feet from the existing Reese Candy #1 and #2 138/69 kV Tap Line to the new West Hershey 69-13 kV Substation.  According to PPL Electric, the West Hershey Tap line which will be located in Derry Township, Dauphin County is required to meet the increasing demand for electricity and improve reliability and operating flexibility in the Derry Township, Dauphin County area.

PPL Electric states that the Derry Township area is currently served from the Hershey 69-13 kV Substation and the South Hershey 69-13 kV Substation via each substation’s associated 13 kV distribution lines.  Presently, these 13 kV distribution lines serve more than 9,300 customers.

PPL Electric states that it has identified four separate issues that will be resolved by the proposed project.  First, loading at the South Hershey 69-13 kV exceeds PPL Electric’s Reliability Principles and Practices (“RP&P”) guidelines for maximum substation capability.  The capability for this substation is 30.4MVA.  The substation reached a peak load of 37.5 MVA during the 2011 summer season and is forecasted to reach a peak load of 37.6 MVA by 2013.  As a result, the South Hershey Substation cannot accommodate any additional load for future growth, and load shedding may be required during peak summer months for maintenance and other outages.

The second issue identified by PPL Electric is that loading at the Hershey 69-13 kV Substation also exceeds PPL Electric’s RP&P guidelines for maximum substation capability.  The capability for this substation is 29.6 MVA.  The substation reached a peak load of 35 MVA during the 2011 summer season and is forecasted to reach a peak load of 38 MVA by 2013.  As a result, the Hershey Substation cannot accommodate any additional load for future growth, and load shedding may be required during peak summer months for maintenance and other outages.

The third issue identified by PPL Electric is that loading at the South Hershey54-1 distribution line exceeds the normal planning guidelines based on PPL Electric’s RP&P.  The existing South Hershey 54-1 13 kV gateway conductor is a #500 KLP copper conductor.  The normal planning guideline for this conductor is 9,100 kVA.  The distribution line reached a peak load of 10,500 kVA during the summer of 2011, which is greater than the normal planning guideline but less than the emergency guideline.  However, overloading the South Hershey 54-1 13 kV line could result in conductor damage or failure, which would interrupt service to approximately 2,175 customers until repairs could be made.

The final issue identified in this area is that loading on the South Hershey 54-5 distribution line exceeds the normal planning guidelines based on PPL Electric's RP&P.  The existing South Hershey 54-5 13 kV getaway conductor is a #500 XLP copper conductor.  The normal planning guideline for this conductor is 9,500 kVA.  The distribution line reached a peak load of 9,700 kVA during the 2011 summer, which is greater than the normal planning guideline but less than the emergency guideline.  However, overloading the South Hershey 54-5 13 kV line could result in conductor damage or failure, which would interrupt service to approximately 1,100 customers until repairs could be made.

In order to resolve the issues explained above, PPL Electric proposes to construct the West Hershey Tap Line.  In conjunction with the proposed West Hershey Tap Line, PPL Electric will construct the new 69-13 kV West Hershey Substation (“West Hershey Substation”) which will be supplied by the Tap Line.  Also, two new 13 kV distribution lines will be installed from the new substation to serve customer load in the area.  These system additions will relieve overloading on existing facilities and increase reliability and operating flexibility.  The proposed West Hershey 69-13 kV Substation will provide critical capacity and improve reliability in the Hershey area.

According to PPL Electric, the two new 13 kV distribution lines will serve part of the load currently being supplied by the South Hershey distribution lines and will reduce peak loading on the South Hershey Substation by 16.3 MVA.  This load transfer will create additional available capacity at the South Hershey Substation and allow it to relieve the distribution lines served by the Hershey Substation.  Once completed, the proposed substation and distribution reinforcements will provide transfer capability between all three substations in the Hershey area during maintenance and other equipment outages.  This Project will resolve all identified RP&P violations in the area.

PPL Electric states that the West Hershey Substation and Tap Lines will be constructed on an approximately 2.19 acre parcel owned by PPL Electric.  No additional right-of-way is required for the construction of the tap lines.  The construction of the West Hershey Tap Line will involve the construction of approximately 150 feet of transmission line.  The Line will be designed and built for double circuit operation.  Initially, however, only a single circuit will be installed, and the line will be operated at 69 kV.  The additional circuit will be added, and the operating voltage will be increased, when load growth in the area makes it appropriate to do so.

The proposed West Hershey Tap Line will require two single-shaft steel monopoles.  The double-circuit tap structure will consist of a high pole that is approximately 110 feet tall and a low pole that is approximately 55 feet tall.  They will be installed on concrete foundations.  The West Hershey Tap Line will initially contain three power conductors and one overhead ground wire.  The power conductors will be 556.5 thousand circular mills (kcmil), 24/7 stranding ACSR.  A 3/8-inch steel overhead ground wire will provide lightning protection for the proposed tap line.

PPL Electric states that the proposed construction of the West Hershey Tap Line will not create any unreasonable risk or danger to the public health or safety.  The proposed project will be designed, constructed, operated, and maintained in a manner that meets or surpasses all applicable National Electrical Safety Code ("NESC") minimum standards and meets all applicable legal requirements.  PPL Electric states that the proposed Project will have minimal incremental impacts on the surrounding area.

PPL Electric also states that the proposed construction was reviewed with representatives of Derry Township and Dauphin County.  The Townships and the County have no objection to the Project.

The total estimated cost to design and construct the transmission portion of the Project is approximately $370,000.  The construction is scheduled to begin in April, 2013 in order to meet a scheduled in-service date of May 2014.

Contemporaneously with the filing of this application, PPL Electric, pursuant to 52 Pa. Code §5.41 and 53 P.S. §10619, filed a Petition with the Commission for a finding that a building to shelter control equipment ("Control Equipment Building") at the proposed West Hershey Substation in Derry Township, Dauphin County, Pennsylvania is reasonably necessary for the convenience or welfare of the public and, therefore, exempt from any local zoning ordinance ("Zoning Petition").  The West Hershey Tap Line will be connected to the proposed West Hershey Substation, including the Control Equipment Building that is the subject of the Zoning Petition.  Issues related to the Zoning Petition are interrelated with the Application.

In the Zoning Petition, PPL Electric requested that the Commission find that the Control Equipment Building is reasonably necessary for the convenience or welfare of the public and, therefore, exempt from Derry Township’s zoning ordinance.  The Zoning Ordinance of 1996 may require a permit prior to the construction of any essential services facilities, which includes public utility facilities, if in Derry Township's opinion, may impose any restriction, condition, or regulation on the construction of the Control Equipment Building.

PPL Electric states that the new West Hershey Substation will include a Control Equipment Building.  The purpose of the proposed Control Equipment Building in the West Hershey Substation is to protect the control equipment from the elements so that the line equipment, and the entire substation, can function properly.  The building will not be intended for human occupancy; there will be no supply of water and no sanitary facilities.  The Control Equipment Building will be contained within the fenced perimeter of the substation.  The West Hershey Substation will be located on a 2.19-acre parcel of land owned in fee by PPL Electric.  The proposed situation of the Control Equipment Building within the fenced perimeter of the substation is the subject of the Zoning Petition filed by PPL Electric.

PPL Electric states that the Pennsylvania Municipalities Planning Code ("MPC") provides, in relevant part, as follows:

“This article shall not apply to any existing or proposed building, or extension thereof, used or to be used by a public utility corporation, if, upon petition of the corporation, the Pennsylvania Public Utility Commission shall, after public hearing, decide that the present or proposed situation of the building in question is reasonably necessary for the convenience or welfare of the public.”

Section 619 of the M P C Act of July 31, 1968, P.L. 805 as, amended, 53 P.S. §10619. Thus, a public utility building is subject to local zoning requirements for buildings unless, upon petition, the Commission determines that the proposed situation of the building in question is reasonably necessary for the convenience and welfare of the public.                  53 P.S. §10619.

PPL Electric asserts that as explained above, the West Hershey Substation, together with the West Hershey Tap Line and additional distribution facilities, are necessary to alleviate projected violations of the RP&P in Derry Township, and will provide additional capacity for future electric system load growth.  The West Hershey Substation must include certain control equipment in order to operate properly, and said equipment must be protected from the elements, which requires the construction of the Control Equipment Building on the West Hershey Substation site.  PPL Electric further states that because the West Hershey Substation is reasonably necessary for the public convenience and welfare, and because the Control Equipment Building is necessary to properly operate the West Hershey Substation, the Commission should find that the Control Equipment Building is reasonably necessary and, therefore, exempt from the Derry Township's local zoning ordinance pursuant to Section 619 of the MPC.  Del-AWARE Unlimited, Inc. v. Pa. P. U C., 513 A.2d 593 (Pa. Cmwlth. 1986).

Further, PPL Electric states that on January 11, 2001, the Commission adopted a policy statement to further the Commonwealth's goal of making agency actions consistent with sound land use planning by considering the impact of its decision upon local comprehensive plans and zoning ordinances.  See 31 Pa. Bull. 951 (Feb. 17, 2001).  Section 69.1101 of the Commission's Regulations provides:

[T]he Commission will consider the impact of its decisions upon local comprehensive plans and zoning ordinances. This will include reviewing applications for:

(1)  Certificates of public convenience.

(2)  Siting electric transmission lines.

(3)  Siting a public utility "building" under

section 619 of the Municipalities Planning

Code (53 P.S. § 10619).

(4)  Other Commission decisions”.

52 Pa Code § 69.1101.

Derry Township has adopted a zoning ordinance, which includes a map on which zoning districts are identified.  See The Zoning Ordinance of Derry Township, Ordinance of January 23, 1996, as amended ("Zoning Ordinance"). The area where the substation will be located is zoned industrial.  With respect to public utility facilities, the Derry Township zoning ordinance defines a public utility building as follows:

A building which is used for the administration or functioning of public or private utility, not including a communications equipment building as defined in this article.

See Zoning Ordinance, Article II § 225-8.

PPL Electric argues that the structure proposed in this zoning petition should be considered a utility building.  Under the Zoning Ordinance, public utility service structures are a permitted use in areas zoned industrial.  See Zoning Ordinance, Article XVIII § 225-73.  Article XVIII imposes certain limitations on the construction of permitted structures in industrial areas, as described in Section 225-76 of the Zoning Ordinance.  Further, the Derry Township Zoning Ordinance recognizes that public utility buildings may be exempt from local regulation, including the height limitation which is

found in Section 225-76.  The Zoning Ordinance states as follows:

The Zoning Hearing Board may grant a special exception to permit public utility service structures to exceed the maximum height regulations when the Board finds that the proposal does not adversely affect the health, safety or welfare of the general public or adversely affect the use and value of abutting properties and when the applicant can demonstrate a public need for the structures that could not be accommodated if the structures were not constructed to a height in excess of this chapter's maximum height limitations. This special exception procedure shall not be available in or applicable to the Airport Safety Zone Overlay District.

See Zoning Ordinance Chapter 27 § 225-172(C).  PPL Electric states that it is unclear if the Derry Township Zoning Ordinance applies to other aspects of public utility service structures, including lot size and dimensions, as well as yard requirements.

PPL Electric argues that under the Zoning Ordinance, if the Commission does not make the finding under Section 619 of the MPC, PPL Electric could be required to obtain a building permit prior to constructing the Control Equipment Building.  § 225-209.  Further, if PPL Electric were required to obtain a building permit prior to construction of the Control Equipment Building, the process, including appeals from adverse determinations, could consume substantial time, which could delay the construction of the West Hershey Substation and transmission lines associated with the project.

Furthermore, the Commission, making the finding under Section 619 of the MPC would not be contrary to the interests of Deny Township.  The proposed Project, including the Control Equipment Building, was reviewed with representatives of Derry Township and Dauphin County.  The Township and the County had no objection to the West Hershey Substation, including the Control Equipment Building. PPL Electric served a copy of this Zoning Petition on Derry Township, the Derry Township Planning Commission, Dauphin County, and the Dauphin County Planning Commission.

Finally, PPL Electric maintains that the West Hershey Substation is necessary in order for PPL Electric to continue to provide adequate and reliable service. The proposed substation will alleviate overloading on the existing substations in Derry Township, as well as on surrounding 13 kV distribution lines providing service to customers in the area.

For these reasons, PPL Electric requests that the Commission find that the Control Equipment Building is reasonably necessary for the convenience or welfare of the public and is, therefore, exempt from the provisions of the Derry Township Zoning Ordinance that may, in Derry Township's opinion, impose any restriction, condition, or regulation on the construction of the Control Equipment Building.

On Saturday, September 22, 2012, notice of the Petition was published in the Pennsylvania Bulletin, 42 Pa.B.6059, setting October 9, 2012 as the deadline for the filing of formal protests and petitions to intervene.

On October 10, 2012, notice of an Initial Prehearing Conference was issued scheduling the prehearing conference for November 27, 2012, at 10:00 am and assigning the matter to ALJ. Susan D. Colwell.  The prehearing conference was held as scheduled, with John H. Isom, Esq., representatives of PPL.  No other entity appeared.

The Commission having conducted a public hearing in this matter after providing notice to the municipal entities where the proposed building will be located.  None of these entities filed a timely protest or petition to intervene indicating that they oppose the relief requested in PPL Electric’s Petition. Therefore, ALJ Susan D. Colwell reassigned the case to the Bureau of Technical Utility Services to be processed as an unprotested petition.

Upon review, the Commission finds that the PPL Electric’s LON and manner in which it was filed conform to the Commission’s regulations of 52 Pa. Code 57.72(d)(1)(vi) because the length of the transmission tap line to be constructed as part of the project is less than two miles.  Also the project is necessary to meet the increasing demand for electricity and improve reliability and operating flexibility in the Derry Township, Dauphin County area.  Above all, the Commission has reviewed the filing and finds it to be consistent with applicable law or Commission policy regarding transmission line siting.  Further, PPL Electric’s Zoning Petition and manner in which it was filed conform to the requirements of 52 Pa. Code §5.41 and 53 P.S. §10619, and because there was no protest to the Petition, we recommend that the Application be approved and the Petition be granted; THEREFORE,

IT IS ORDERED:

# 1. That the Application filed by PPL Electric Utilities Corporation for the siting and construction of the West Hershey #1 & #2 138/69 kV Tap Line in Derry Township, Dauphin County, Pennsylvania is hereby approved.

# 2. That the Petition of PPL Electric Utilities Corporation for a finding that a building to shelter control equipment at the proposed West Hershey 69-123 kV Substation in Derry Township, Dauphin County, Pennsylvania is reasonably necessary for the convenience or welfare of the public and, therefore exempt from any local zoning ordinance, is hereby granted.

BY THE COMMISSION,

# Rosemary Chiavetta

Secretary

(SEAL)

# ORDER ADOPTED: February 14, 2013

# ORDER ENTERED: February 14, 2013

Kcmil wire size is the equivalent cross sectional area in thousands of circular mils.  A circular mil is the area of a

circle with a diameter of one thousandth (0.001) of an inch.

Aluminum conductor steel reinforced.

PPL Electric believes its control equipment building is not a "building" but, rather, is part of its substation facilities. Therefore, PPL Electric's control equipment building is exempt from local zoning requirements. See, e.g., Duquesne Light Co. v. Upper St. Clair Township, 377 Pa. 323, 334-35, 105 A.2d 287, 292 (1954). This Zoning Petition is being filed as a precaution in the event that the Commission were to determine that the control equipment building is not a facility and, therefore, potentially subject to local zoning ordinances.