# PENNSYLVANIA

# PUBLIC UTILITY COMMISSION

# Harrisburg, PA 17105-3265

# Public Meeting held February 28, 2013

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Jr., Vice Chairman

Wayne E. Gardner

# James H. Cawley

# Pamela A. Witmer

# Letter of Notification of PPL Electric

# Utilities Corporation, Filed Pursuant to

# 52 Pa. Code Chapter 57 Subchapter G,

# for Approval of the Siting and Construction                                        A-2012-2338936

# of an Extension of the Existing Lycoming-

# Lock Haven #4 138/69 kV Transmission

# Line in Castanea Township, Clinton

# County, Pennsylvania

# Petition of PPL Electric Utilities Corporation

# For a Finding that a Building to Shelter

# Control Equipment at the Lock Haven                                                 P-2012-2338928

# 138/69 kV Switchyard to be Constructed In

# Castanea Township, Clinton County,

# Pennsylvania is Reasonably Necessary for

# the Convenience or Welfare of the Public.

# ORDER

BY THE COMMISSION:

On December 12, 2012, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to Chapter 57, Subchapter G of the Commission’s regulations at 52 Pa. Code §57.72(d)(1)(vi), governing the siting and construction of high voltage transmission lines.  Section 57.72 authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

- An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

- An HV line which is proposed to be located entirely within a public road.

- An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- An HV line having a proposed route of 2 miles or less.

Copies of the LON were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Clinton County Planning Commission, Clinton County Board of Commissioners, Castanea Township Planning Commission, Castanea Township Board of Supervisors and other interested parties as listed in the Certificate of Service.  No protest was filed and no hearing was held.

PPL Electric requests Commission approval to extend the existing Lycoming – Lock Haven #4 138/69 kV Transmission Line (“Lycoming-Lock Haven Line”) by approximately 1,300 feet.  A new 138/69 kV Switchyard will be constructed into which the extended line will be re-terminated.  The proposed line extension will be routed in a southerly direction from its current termination point at the existing Lock Haven 69 kV Switchyard to a new termination point at the proposed new Lock Haven 138/69 kV Switchyard.  PPL Electric maintains that the extension, which will be located in Castanea Township, Clinton County is required to resolve reliability and low voltage issues, and also improve operating flexibility in the area.

According to PPL Electric, the Lock Haven 69-12 kV Substation and the Lock Haven 69 kV Switchyard, including its seven 69 kV transmission lines, serve approximately 6,800 customers in the Castanea Township and Lock Haven areas.  The Lycoming - Lock Haven #4 138/69 kV line, is designed to operate at 138 kV, but it currently operates at 69 kV.  The existing 69 kV switchyard enables PPL Electric to switch transmission loads among the seven 69 kV lines and also provides electric power to the Lock Haven 69-12 kV distribution substation.  There is no source of bulk electric power available in the Lock Haven area.  As a result, four 69 kV transmission lines are required to connect the existing Lock Haven 69 kV Switchyard and the Lycoming 230-69 kV Substation.  One 69 kV transmission line connects the Lock Haven 69 kV Switchyard and the Sunbury 230-138-69 kV Substation.  Those five 69 kV lines are, and will continue to be, operated in a "networked" configuration.  This networked configuration provides a source of power to the Lock Haven 69 kV Switchyard from both the Lycoming and Sunbury regional substations.  However, these two sources of electric power are located approximately 25 miles to the northeast and 40 miles to the southeast of the Lock Haven 69 kV Switchyard, respectively.

PPL Electric states that under the existing electrical arrangement of the Lock Haven 69 kV Switchyard, voltage violations would result at multiple 69 kV substation buses.  Three 69 kV line segments would become loaded above their emergency ratings if a certain contingency were to occur.  These buses and lines are located throughout the Lock Haven area.

Further, PPL Electric states that it has identified six different contingencies that would cause a voltage change that exceeds the PPL Electric "Reliability Principles & Practices" ("RP&P") guidelines.  Those guidelines require that any voltage change at a bus be limited to no more than a 5 percent difference from the pre-contingency voltage.  Also, the bus voltage after a contingency occurs must remain within the planning range of 62 kV to 68 kV.

PPL Electric states that it has also identified five different contingencies that would cause multiple line segments to be loaded above their emergency ratings.  The RP&P guidelines state that no electrical facility may be loaded above its emergency rating after a contingency occurs.   Even under a light load scenario, two of the five contingencies would produce voltages at multiple buses that would both exceed the allowed 5 percent difference and fall below the lower voltage limit.

PPL Electric states that analysis of the outcomes of the six contingencies shows the median voltage change to be 7.7 percent.  The number of customers that would be interrupted if three of these contingencies were to occur ranges from approximately 2000 to 8800 customers.  Three of the six contingencies would not interrupt customers initially but would cause voltages at local 69 kV buses to drop below the lower limit of 62 kV.  That outcome would require the Transmission System Operator to shed load and ultimately interrupt customers connected to those 69 kV lines.  This violation of the RP&P will not occur when the new breaker-and-a-half switchyard arrangement is operational.

PPL Electric states that the seven-breaker ring-bus arrangement in the existing yard cannot be modified in its present location to create a switchyard of standard design due to the lack of available space.  The seven-breaker ring-bus is the major reason why the voltage RP&P violations stated above occur.  In a ring-bus arrangement, when one transmission line experiences a contingency, the circuit breakers on either side of that line termination will "open" in order to remove that line from service.  The opening of those two circuit breakers "separates” the ring.  The remaining transmission lines that are still in-service lose the electrical support provided by an intact ring-bus, and in some scenarios the remaining lines lose the electric support provided by the regional substations at Lycoming and Sunbury.  The ring-bus is electrically weakened, and the result is either overloaded line segments or bus voltages that drop below the lower planning and operating limits. PPL Electric current design standards now require a breaker-and-a-half arrangement.

Further, because of the existing ring-bus design at the switchyard, the ability to perform periodic maintenance on substation equipment in the future will become more and more difficult due to of the system configuration that results.  A breaker out for maintenance and a subsequent line outage may lead to overloads and unacceptable voltage levels, even under lighter load periods.  The ultimate consequence would be that periodic maintenance of certain station equipment would not be allowed because of the harm it would cause to the electrical grid.

In order to resolve the issues discussed above, PPL Electric seeks PUC approval to construct the Lycoming - Lock Haven #4 138/69 kV line extension so that the existing transmission line can be re-connected from the existing yard into the new yard. After the Commission's approval of the new line extension, PPL Electric will also construct the Lock Haven 138/69 kV switchyard that will terminate the line extension and six other 69 kV lines.  PPL Electric maintains that these system additions will mitigate maintenance constraints that currently exist, while increasing reliability and operating flexibility in the local area, which would provide the Transmission System Operator more options to reconfigure the transmission lines when maintenance is being performed.

PPL Electric states that the Lycoming - Lock Haven #4 138/69 kV line extension, will be constructed on land owned in fee by PPL Electric.  No additional land rights are required for the Project.  Construction of the line extension will require the installation of approximately three steel pole structures on foundations and two direct-embedded steel pole structures.  The structures will range in height from approximately 75 to 100 feet. The new section of transmission line will consist of three 556.5 kcmil, 24/7 stranding, aluminum conductor steel reinforced ("ACSR") power conductors.  One 3/8 inch steel overhead ground wire will be installed to provide lightning protection for the proposed line extension.  The proposed line extension will be designed as a single-circuit 138 kV pole-line, but it will be initially operated at 69 kV.  In the future, when customer load increases to a level that makes a higher voltage to serve the local area appropriate, it will then be converted to 138kV operation.

PPL Electric states that the proposed extension of the Lycoming-Lock Haven Line will not create any unreasonable risk or danger to the public health or safety.  The proposed project will be designed to, and will generally exceed, minimum National Electrical Safety Code ("NESC") standards.  Further, PPL Electric states that the proposed Project will have minimal incremental impacts on the surrounding area due to the facts that the Project is located in an area which contains existing PPL Electric facilities and that no additional land rights are required.

According to PPL Electric, the Project was reviewed with representatives of Castanea Township and Clinton County.  The Township and the County had no objection to the Project.

The total estimated cost the construction of the Lycoming-Lock Haven #4 138/69 kV Transmission Line Extension portion of the Project is $516,000, which is being paid by PPL Electric.  The construction is scheduled to begin in December 2013 in order to meet a scheduled in-service date of June 2015.

Contemporaneously with the filing of this application, PPL Electric, pursuant to 52 Pa. Code §5.41 and 53 P.S. §10619, filed a Petition with the Commission for a finding that a building to shelter control equipment ("Control Equipment Building") at the proposed Lock Haven 138/69 kV Switchyard ("Switchyard") in Castanea Township, Clinton County, Pennsylvania is reasonably necessary for the convenience or welfare of the public and, therefore, exempt from any local zoning ordinance ("Zoning Petition").  The Lycoming-Lock Haven Line extension will be re-terminated into the proposed Lock Haven Switchyard.  Issues related to the Zoning Petition are interrelated with this Application.

PPL Electric states that the new Lock Haven Switchyard will include a Control Equipment Building.  The purpose of the proposed Control Equipment Building in the Lock Haven Switchyard is to protect the control equipment from the elements so that the line equipment, and the entire substation, can function properly.  The building will not be intended for human occupancy; there will be no supply of water and no sanitary facilities.  The Control Equipment Building will be contained within the fenced perimeter of the Switchyard.  The Lock Haven Switchyard will be located on an approximately 16-acre parcel of land owned by PPL Electric.  The proposed situation of the Control Equipment Building within the fenced perimeter of the switchyard is the subject of the Zoning Petition filed by PPL Electric.

PPL Electric states that the Pennsylvania Municipalities Planning Code ("MPC") provides, in relevant part, as follows:

“This article shall not apply to any existing or proposed building, or extension thereof, used or to be used by a public utility corporation, if, upon petition of the corporation, the Pennsylvania Public Utility Commission shall, after public hearing, decide that the present or proposed situation of the building in question is reasonably necessary for the convenience or welfare of the public.”

Section 619 of the M P C Act of July 31, 1968, P.L. 805 as, amended, 53 P.S. §10619. Thus, a public utility building is subject to local zoning requirements for buildings unless, upon petition, the Commission determines that the proposed situation of the building in question is reasonably necessary for the convenience and welfare of the public.                  53 P.S. §10619.

PPL Electric asserts that the Lock Haven Switchyard must include certain control equipment in order to operate properly, and said equipment must be protected from the elements.  The purpose of the Control Equipment Building at the Lock Haven Switchyard is to provide that protection.  Because the Lock Haven Switchyard is reasonably necessary for the public convenience and welfare and because the Control Equipment Building is necessary to properly operate the Lock Haven Switchyard, the Commission should find that the Control Equipment Building is reasonably necessary and, therefore, exempt from the Castanea Township's local zoning ordinance pursuant to Section 619 of the MPC.  Del-AWARE Unlimited, Inc. v. Pa. P. U C., 513 A.2d 593 (Pa. Cmwlth. 1986).

Further, PPL Electric states that on January 11, 2001, the Commission adopted a policy statement to further the Commonwealth's goal of making agency actions consistent with sound land use planning by considering the impact of its decision upon local comprehensive plans and zoning ordinances.  See 31 Pa. Bull. 951 (Feb. 17, 2001).  Section 69.1101 of the Commission's Regulations provides:

[T]he Commission will consider the impact of its decisions upon local comprehensive plans and zoning ordinances. This will include reviewing applications for:

(1)  Certificates of public convenience.

(2)  Siting electric transmission lines.

(3)  Siting a public utility "building" under

section 619 of the Municipalities Planning

Code (53 P.S. § 10619).

(4)  Other Commission decisions”.

52 Pa Code § 69.1101.

Castanea Township has adopted a zoning ordinance, the Castanea Township Zoning Ordinance of 2010, ("Zoning Ordinance").  The Zoning Ordinance, among other things, divides the township into zoning districts.  The location where PPL Electric proposes to construct the Lock Haven Switchyard is designated partially as a "High Density Residential" District and partially as a "Medium Density Residential" District.

Under the Zoning Ordinance, the Switchyard, including the Control Equipment Building, apparently would be a "utility supply facility," which is defined in pertinent part as:

Facilities, buildings and/or structures constructed and maintained by public utility companies . . . which are necessary for the provision of utility services to the general public.  Such facilities shall include, but need not be limited to, electrical or telephone substations . . . or similar facilities."

Also, under the Zoning Ordinance, a utility supply facility is a "conditional use" in a High or Medium Density Residential zoning district, Section 403 of the Zoning Ordinance.  Utility Supply Facilities are permitted only upon approval by the Township Supervisors, Section 529 of the Zoning Ordinance.

PPL Electric argues that one difficulty with the Zoning Ordinance is that it is impossible to determine whether a utility supply facility would be approved.  Under the Zoning Ordinance, utility supply facilities are evaluated on a case-by-case basis.  The Zoning Ordinance specifically provides that the Township Supervisors can decide during the evaluation what the setback and building coverage requirements will be, whether the utility supply facility is compatible in appearance with the surrounding area and whether additional safety precautions arc needed, whether buffers, screening or fencing arc required.  PPL Electric maintains that the process of obtaining a zoning permit, including possible appeals from the Board's decision, can be a long and time-consuming process, which could delay completion of the Project until long after the date when the Project is required to be in service in order to avoid conditions which could damage facilities and cause interruption of service to customers.  The risk of delays is especially great under the Zoning Ordinance because the requirements to obtain a building permit for a utility supply facility are unknown in advance.  In addition, the requirements for a building permit could add to the cost of the Project, delay the Project or interfere with its operations.

As indicated in the attached certificate of service, PPL Electric served a copy of this Zoning Petition on Castanea Township, the Castanea Township Planning Commission, Clinton County, and the Clinton County Planning Commission.  PPL Electric states that the proposed Project, including the Switchyard, was reviewed with representatives of Castanea Township and Clinton County.  The Township and the County had no objection to the Project, including the Switchyard.

PPL Electric argues that the proposed Switchyard Control Equipment Building, together with the related work on transmission and distribution facilities, will enable it to continue to provide reliable and adequate service in the future.  The new Lock Haven Switchyard is needed to improve the reliability of electric service in the Lock Haven and Castanea area.

For these reasons, PPL Electric requests that the Commission find that the Control Equipment Building is reasonably necessary for the convenience or welfare of the public and is, therefore, exempt from the provisions of the Castanea Township Zoning Ordinance.

On Saturday, December 29, 2012, notice of the Petition was published in the Pennsylvania Bulletin, 42 Pa.B.7882, setting January 14, 2013 as the deadline for the filing of formal protests and petitions to intervene.

On December 19, 2012, notice of an Initial Prehearing Conference was issued scheduling the prehearing conference for January 23, 2013, at 10:00 am and the matter was assigned to ALJ. David A. Salapa. The prehearing conference was held as scheduled, with John H. Isom, Esq., representing PPL.  No other entity appeared.

The Commission having conducted a public hearing in this matter after providing notice to the municipal entities where the proposed building will be located and notice to the Commonwealth agencies that may have interest in this matter.  None of these entities filed a timely protest or petition to intervene indicating that they oppose the relief requested in PPL Electric’s Petition.  Therefore, ALJ David A. Salapa reassigned the case to the Bureau of Technical Utility Services to be processed as an unprotested petition.

Upon review, the Commission finds that the PPL Electric’s LON and manner in which it was filed conform to the Commission’s regulations of 52 Pa. Code 57.72(d)(1)(vi) because the length of the transmission line to be constructed as part of the project is less than two miles.  Also the project is necessary to meet the increasing demand for electricity and improve reliability and operating flexibility of PPL Electric’s system in the Castanea Township, Clinton County area.  Above all, the Commission has reviewed the filing and finds it to be consistent with applicable law or Commission policy regarding transmission line siting.  Further, PPL Electric’s Zoning Petition and manner in which it was filed conform to the requirements of 52 Pa. Code §5.41 and 53 P.S. §10619, and because there was no protest to the Petition, the Application is approved and the Petition is granted; THEREFORE,

IT IS ORDERED:

# 1.  That the Application filed by PPL Electric Utilities Corporation for the siting and construction of an extension to the existing Lycoming-Lock Haven #4 138/69 kV Line in Castanea Township, Clinton County, Pennsylvania is hereby approved.

# 2.  That the Petition of PPL Electric Utilities Corporation for a finding that a building to shelter control equipment at the proposed Lock Haven 138/69 kV Switchyard in Castanea Township, Clinton County, Pennsylvania is reasonably necessary for the convenience or welfare of the public and, therefore exempt from any local zoning ordinance, is hereby granted.

# 3.  That this case at Docket Nos. A-2012-2338936 and P-2012-2338928 be closed.

BY THE COMMISSION,

# Rosemary Chiavetta

Secretary

(SEAL)

# ORDER ADOPTED: February 28, 2013

# ORDER ENTERED: February 28, 2013

Electric power facilities operating at voltages greater than 100 kV.

Unplanned outage of a line, bus, transformer, or other power system clement.

"Kcmil is one thousand circular mils. A circular mil is the cross-sectional area of a wire one mil in diameter,

where I kcmil = 0.5067 mm2.

PPL Electric believes its control equipment building is not a "building" but, rather, is part of its substation facilities. Therefore, PPL Electric's control equipment building is exempt from local zoning requirements. See, e.g., Duquesne Light Co. v. Upper St. Clair Township, 377 Pa. 323, 334-35, 105 A.2d 287, 292 (1954). This Zoning Petition is being filed as a precaution in the event that the Commission were to determine that the control equipment building is not a facility and, therefore, potentially subject to local zoning ordinances.

A switchyard is a type of substation.