# PENNSYLVANIA

# PUBLIC UTILITY COMMISSION

# Harrisburg, PA 17105-3265

# Public Meeting held July 16, 2013

Commissioners Present:

Robert F. Powelson, Chairman

John F. Coleman, Jr., Vice Chairman

Wayne E. Gardner

# James H. Cawley

# Pamela A. Witmer

# Letter of Notification of PPL Electric Utilities Corporation, Filed Pursuant to 52 Pa. Code Chapter 57 Subchapter G,

# For Approval of the Siting and Construction                                        A-2013-2347931

# of the Long Pond #1 and #2 138/69 kV

# Transmission Tap Line in Tobyhanna

# Township, Monroe County, Pennsylvania

# Petition of PPL Electric Utilities Corporation

# For a Finding that a Building to Shelter Control

# Equipment at the proposed Long Pond 69-12 kV 			P-2013-2347936

# Substation, to be Constructed in Tobyhanna

# Township, Monroe County, Pennsylvania is

# Reasonably Necessary for the Convenience or

# Welfare of the Public.

# ORDER

BY THE COMMISSION:

On February 12, 2013, PPL Electric Utilities Corporation (“PPL Electric”) filed a Letter of Notification (“LON”) pursuant to Chapter 57, Subchapter G of the Commission’s regulations at 52 Pa. Code §57.72(d)(1)(vi), governing the siting and construction of high voltage transmission lines with a proposed route of 2 miles or less.  Section 57.72 in general authorizes the abbreviated “Letter of Notification” siting application process in lieu of an application for the following:

- An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character, design, or configuration, of the proposed HV line does not substantially alter the right-of-way.

- An HV line which is proposed to be located entirely within a public road.

- An HV line which is proposed to be located entirely within applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- An HV which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- An HV line having a proposed route of 2 miles or less.

Copies of the LON were served in accordance with Section 57.72(d) (3) and 57.74 (b), (c) on the PA Department of Transportation, PA Historical and Museum Commission, PA Department of Environmental Protection, Monroe County Planning Commission, Monroe County Board of Commissioners, Tobyhanna Township Planning Commission, Tobyhanna Township Board of Supervisors and other interested parties as listed in the Certificate of Service.  No protest was filed and no hearing was held.

PPL Electric requests Commission approval for the construction of the Long Pond #1 and #2 138/69 kV Transmission Tap Line (“Long Pond Tap Line”) in Tobyhanna Township, Monroe County, Pennsylvania.  The proposed Tap Line is being constructed in order to supply the planned Long Pond 69-12 kV Substation ("Long Pond Substation").  The Project, including the Tap Line, the Substation and related distribution line work, is needed to address service issues identified using PPL Electric’s Reliability Principles and Practices (RP&P) and is required to meet the increasing demand for electricity and improve reliability of service in the Tobyhanna Township area of Monroe County.

PPL Electric states that the Long Pond Tap Line will require the construction of approximately 650 feet of transmission line extending from the Jackson-Wagners 138/69 kV Transmission Line to the new Long Pond 69-12 Substation.  The Tap Line will be designed and built for double-circuit operation.  Initially, however, only a single circuit will be installed, and the line will be operated at 69 kV.  The additional circuit will be added, and the operating voltage will be increased, when load growth in the area makes it appropriate to do so.

According to PPL Electric, the Tobyhanna Township area is presently served from the Lake Naomi 69-12 kV, Mount Pocono 69-12 kV and Wagners 69-12 kV Substations via 12 kV distribution lines.  The associated 12 kV distribution lines, which currently serve the area, include the Wagners 68-1, Mount Pocono 64-6, and the Lake Naomi 86-1, 86-2, and 86-4 distribution lines.  These l2 kV lines serve over 7,500 customers in the Tobyhanna Township area.  PPL Electric has identified six separate issues in the Tobyhanna Township area of Monroe County, that will be resolved or improved by the proposed Project.

First, peak load on the Wagners 68-1 distribution line is projected to exceed the normal planning guidelines based on PPL Electric's RP&P.  The existing Wagners 68-1 12 kV distribution line uses 336 aluminum conductors.  The planning guideline peak load for this type of conductor is 10,000 kVA (kilovolt Ampere).  The 2013-2014-winter peak load is projected to be 11,300 kVA.  Overloading the Wagners 68-1 12 kV line could result in conductor damage or failure which would interrupt service to approximately 1,650 customers until repairs could be completed.  As a result, the existing distribution line cannot accommodate future load growth in the area.

Second, the peak load on the Lake Naomi 86-1 distribution line is projected to exceed the normal planning guidelines based on PPL Electric's RP&P.  The existing Lake Naomi 86-1 12 kV distribution line uses 477 aluminum conductors.  The planning guideline peak load for such conductors is 11,000 kVA.  The 2013-2014-winter peak load is projected to be 11,900 kVA.  Overloading the Lake Naomi 86-1 12 kV line could result in conductor damage or failure which would interrupt service to approximately 1,200 customers until repairs could be completed.  As a result, the existing distribution line cannot accommodate future load growth in the area.

Third, the peak load on the Lake Naomi 86-2 distribution line is projected to exceed the normal planning guidelines based on PPL Electric's RP&P.  The existing Lake Naomi 86-2 12 kV distribution line uses 477 aluminum conductors.  The planning guideline peak load for such conductors is 11,000 kVA.  The winter 2014 peak load is projected to be 11,300 kVA.  Overloading the Lake Naomi 86-2 12 kV line could result in conductor damage or failure which would interrupt service to approximately 1,950 customers until repairs could be completed.  As a result, the existing distribution line cannot accommodate future load growth in the area.

Fourth, the peak load on the Lake Naomi 86-4 distribution line is projected to exceed the normal planning guidelines based on PPL Electric's RP&P.  The existing Lake Naomi 86-4 12 kV distribution line uses 477 aluminum conductors.  The planning guideline peak load for such conductors is 11,000 kVA.  The 2013-2014-winter peak load is projected to be 11,100 kVA.  Overloading the Lake Naomi 86-4 12 kV line could result in conductor damage or failure which would interrupt service to approximately 2,100 customers until repairs could be completed.  As a result, the existing distribution line cannot accommodate future load growth in the area.

Fifth, the existing Wagners 68-1, Lake Naomi 86-2, and 86-4 distribution lines exceed PPL Electric's RP&P guidelines for customer count per line.  The RP&P guideline provides that no more than 1,300 customers should be served from a 12 kV circuit.  Presently these three circuits serve approximately 1,650, 1,950, and 2,100 customers, respectively.

Sixth, due to heavy loading of the distribution lines, the existing system configuration has limited capability to transfer load to the adjoining distribution lines so that service is not interrupted during scheduled outages for maintenance and unscheduled outages.  Therefore, if one of the existing distribution lines were to fail or require maintenance, customers could not be served from a different distribution line.  Consequently, they would be without service until the work could be completed.

In order to resolve the issues discussed above, PPL Electric seeks to construct the Long Pond Tap Line and the Long Pond Substation.  In addition, two new 12 kV distribution lines will be constructed from the new substation to serve customer load in the area.  PPL Electric asserts that these system additions will relieve loading and increase reliability and operating flexibility.  The new Long Pond 69-12 kV Substation will serve approximately 2,830 customers and 11.8 MVA of load.  The new lines will reduce the number of customers served per line.  As an additional benefit, the new lines will also reduce the circuit length of the distribution lines in the area.  The system additions, and the accompanying reductions in number of customers per circuit and circuit length, will reduce the customers' exposure to outages and reduce the number of customers affected by an outage.

PPL Electric states that the Long Pond Tap Line will be constructed on two separate parcels of land.  PPL Electric requires a small section of new 100 foot wide right-of-way on one of the parcels to construct the Project.  The property owner has signed a right-of-way agreement conveying the required easement to PPL Electric.  The second parcel of land on which a portion of the Long Pond Tap Line and Substation will be constructed is owned in fee by PPL Electric.

PPL Electric states that the proposed Long Pond Tap Line will involve the installation of a total of six steel structures and the removal of three wood pole structures. One new structure will be a direct embedded high tap pole structure, approximately 97 feet in height; guy anchors will be installed to support this structure.  This structure will replace an existing wood pole.  The two additional wood pole structures, one on each side of the high tap pole structure, will be replaced in approximately the same location with direct embedded steel poles which will be approximately 70 feet in height.  In addition, a direct embedded steel pole, approximately 70 feet in height for a load sectionalizing air break switch, will be constructed.  The remaining two structures will be direct embedded single steel poles approximately 79 feet in height.  They will be supported by guy wires.  The Long Pond Tap Line will initially contain three power conductors and one optic overhead ground wire ("OPGW").  The power conductors will be 556.5 kcmil, 24/7 strand aluminum conductor steel reinforced.  A 0.567 inch OPGW will provide lightning protection for the proposed tap line and communications to the substations.  In the future, when increased demand requires the installation of a second circuit, the additional power conductors will be installed.  The second circuit will be identical to the first circuit.

PPL Electric states that the proposed Long Pond Tap Line will not create any unreasonable risk or danger to the public health or safety.  The proposed project will be designed to, and will generally exceed, minimum National Electric Safety Code ("NESC") standards.  Further, PPL Electric states that the proposed Project will have minimal incremental impacts on the surrounding area due to the fact that the Project is located in an area that already contains existing PPL Electric facilities.

According to PPL Electric, the Project was reviewed with representatives of Tobyhanna Township and Monroe County.  The Township and the County had no objection to the Project.

The total estimated cost to design and construct the transmission line portion of the Project is $460,000.  The construction is scheduled to begin in February 2014 in order to meet a scheduled in-service date of November 2014.

Contemporaneously with the filing of this application, PPL Electric, pursuant to 52 Pa. Code §5.41 and 53 P.S. §10619, filed a Petition with the Commission for a finding that a building to shelter control equipment ("Control Equipment Building") at the proposed Long Pond 69-12 kV Substation ("Long Pond Substation ") in Tobyhanna Township, Monroe County, Pennsylvania is reasonably necessary for the convenience or welfare of the public and, therefore, exempt from any local zoning ordinance ("Zoning Petition").  Issues related to the Zoning Petition are interrelated with this Application.  The purpose of the Long Pond #1 and #2 138/69 kV Tap Line is to supply the Long Pond Substation.

PPL Electric states that the proposed Long Pond Substation will include a Control Equipment Building.  The purpose of the proposed Control Equipment Building in the Long Pond Substation is to protect the control equipment from the elements so that the line equipment, and the entire substation, can function properly.  The building will not be intended for human occupancy; there will be no supply of water and no sanitary facilities.  The Control Equipment Building will be contained within the fenced perimeter of the Long Pond Substation.  The Long Pond Substation will be located on an approximately 20-acre parcel of land owned in fee by PPL Electric.  The proposed situation of the Control Equipment Building within the fenced perimeter of the Long Pond Substation is the subject of the Zoning Petition filed by PPL Electric.

PPL Electric states that the Pennsylvania Municipalities Planning Code ("MPC") provides, in relevant part, as follows:

“This article shall not apply to any existing or proposed building, or extension thereof, used or to be used by a public utility corporation, if, upon petition of the corporation, the Pennsylvania Public Utility Commission shall, after public hearing, decide that the present or proposed situation of the building in question is reasonably necessary for the convenience or welfare of the public.”

Section 619 of the MPC Act of July 31, 1968.  P.L. 805 as, amended, 53 P.S. §10619.

Thus, a public utility building is subject to local zoning requirements for buildings unless, upon petition, the Commission determines that the proposed situation of the building in question is reasonably necessary for the convenience and welfare of the public.                   53 P.S. §10619

As explained above, PPL Electric asserts that the Long Pond Substation is necessary to increase the reliability of service in the Tobyhanna area.  In order to operate properly, the Long Pond Substation must have certain control equipment and said control equipment must be protected from the elements.  The purpose of the Control Equipment Building at the Long Pond Substation is to provide that protection.  Because the Long Pond Substation is reasonably necessary for the public convenience and welfare and because the Control Equipment Building is necessary to properly operate the Long Pond Substation, the Commission should find that the Control Equipment Building is reasonably necessary and, therefore, exempt from the Tobyhanna Township's local zoning ordinance pursuant to Section 619 of the MPC.  Del-AWARE Unlimited, Inc. v. Pa. P.U. C.  513 A.2d 593 (Pa. Cmwlth. 1986).

Further, PPL Electric states that on January 11, 2001, the Commission adopted a policy statement to further the Commonwealth's goal of making agency actions consistent with sound land use planning by considering the impact of its decision upon local comprehensive plans and zoning ordinances.  See 31 Pa. Bull. 951 (Feb. 17, 2001).  Section 69.1101 of the Commission's Regulations provides:

[T]he Commission will consider the impact of its decisions upon local comprehensive plans and zoning ordinances. This will include reviewing applications for:

(1)  Certificates of public convenience.

(2)  Siting electric transmission lines.

(3)  Siting a public utility "building" under       section 619 of the Municipalities Planning     Code (53 P.S. §10619).

(4)  Other Commission decisions.

52 Pa. Code § 69.1101

PPL Electric states that Tobyhanna Township has adopted a zoning ordinance.  See the Tobyhanna Township Zoning Ordinance of 1995, ("Tobyhanna Zoning Ordinance").

Under the Tobyhanna Zoning Ordinance, public utility uses are permitted in any district with a special exception permit.  Specifically, Section 155-89 of the Tobyhanna Zoning Ordinance provides:

Public utility uses, such as dial equipment centers, high-voltage transmission lines, towers, substations and other proposed installations necessary to serve the region or area, as opposed to  surrounding properties, may be permitted in any zoning district with a special exception permit.  No special exception permit shall be issued unless the Zoning Hearing Board shall determine that:

- The proposed installation in a specific location is necessary and convenient for the efficiency of the public utility system or the satisfactory and convenient provision of service by the utility to the neighborhood, area or region in which the particular use is to be located.

- The design of any building in connection with such facility conforms to the general character of the area and will not adversely affect the safe and comfortable enjoyment of property rights of the zone in which it is located.

- Adequate and attractive fences, noise barriers and other     safety devices will be provided.

- A buffer strip five feet in width and screening are provided and will be   periodically maintained.

- Adequate off-street parking will be provided to meet the needs of the use.

- All of the area, yard and building coverage requirements of the respective zones will be met.

- All other items or details of construction or location are consistent with the intent of this chapter.

PPL Electric explains that Tobyhanna Zoning Ordinance purports to authorize the Zoning Hearing Board to consider, among other things, the need for the Substation, including the Control Equipment Building, the siting of the Substation, including the Control Equipment Building, the design of the Control Equipment Building and safety measures.  Under the Public Utility Code, all of these matters are subject to the exclusive jurisdiction of the Commission and beyond the jurisdiction of the Tobyhanna Township Zoning Hearing Board regarding public utility substations, including control equipment buildings.

Further, Section 155-72 of the Tobyhanna Zoning Ordinance also provides, regarding special exceptions, that:

Where this chapter has stated, special exceptions, may be granted or denied by the Board, pursuant to express standards and criteria. In granting a special Exception, the Board may attach such reasonable conditions and safeguards, in addition to those expressed in this chapter, as it may deem necessary to implement the purposes of the Municipalities Planning Code.

Thus, under the Tobyhanna Zoning Ordinance, the Zoning Hearing Board may impose other conditions on the issuance of a special exception, which could place additional burden on PPL Electric or interfere with the operation of the substation.

In addition to the foregoing, a zoning permit must be obtained prior to the construction, reconstruction, addition, conversion, alteration, enlargement, repair, moving, demolition or use of any building, structure, or portion thereof.  A zoning permit is also required prior to the use or change in use of a building, structure, or land.  See TOBYHANNA TOWNSHIP ZONING ORDINANCE Article 8, Section 800.1.  Further, Tobyhanna Zoning Ordinance, Section 155.131, provides that a use certificate is required before use of any structure or land.

PPL Electric argues that based on the foregoing, in the absence of a finding by the Commission under Section 619 of the MPC, it is unlawful under the Tobyhanna Zoning Ordinance for PPL Electric to commence work on the Control Equipment Building without first obtaining a building permit from Tobyhanna Township.  Further, if PPL Electric’s proposed Control Equipment Building were subject to the Tobyhanna Zoning Ordinance, PPL Electric would be required to obtain a special exception for the Control Equipment Building, as well as a zoning permit.  In order to obtain such approvals, PPL Electric would have to follow the permitting procedures set forth in the Zoning Ordinance, including the payment of fees.  Furthermore, If PPL Electric were required to obtain zoning and/or use permits prior to the construction of the Control Equipment Buildings, the process, including any appeals from adverse determinations, could delay the Long Pond Project.

PPL Electric states that the proposed Project, including the Substation, was reviewed with representatives of Tobyhanna Township and of Monroe County.  The Township and the County had no objection to the Project, including the Substation.  PPL Electric served a copy of this Zoning Petition on Tobyhanna Township Board of Supervisors, the Tobyhanna Township Zoning Hearing Board, Monroe County Commissioners, and the Monroe County Planning Commission.

Finally, PPL Electric maintains that the Control Equipment Building at the Long Pond Substation is necessary in order for PPL Electric to continue to provide adequate and reliable service.  The proposed Control Equipment Building, together with the related work on transmission and distribution facilities, will enable PPL Electric to continue to provide reliable and adequate service in the future.  The Long Pond Substation is needed to improve the reliability of electric service in the Tobyhanna Township area.

For these reasons, PPL Electric requests that the Commission find that the Control Equipment Building at the proposed Long Pond Substation is reasonably necessary for the convenience or welfare of the public and is, therefore, exempt from the requirements of the Tobyhanna Township Zoning Ordinance.

The Petition was served upon the Commission’s Bureau of Investigation & Enforcement, the Office of Consumer Advocate, the Office of Small Business Advocate, the Emerald Lakes Association, Inc., and as stated earlier, upon the Monroe County Planning Commission, Monroe County Commissioners, Tobyhanna Township Planning Commission, and the Tobyhanna Township Board of Supervisors.

On February 27, 2013, notice of an Initial Prehearing Conference was issued scheduling the prehearing conference for April 4, 2013, at 10:00 am and the matter was assigned to ALJ Elizabeth H. Barnes.  The prehearing conference was held as scheduled, with PPL Electric in attendance.  No other entity entered an appearance, filed a protest, filed a petition to intervene, or appeared at the prehearing conference.

The Commission conducted a public hearing in this matter after providing notice to the municipal entities where the proposed building will be located and notice to the Commonwealth agencies that may have interest in this matter.  None of these entities filed a timely protest or petition to intervene indicating that they oppose the relief requested in PPL Electric’s Petition.  Therefore, ALJ Elizabeth H. Barnes reassigned the case to the Bureau of Technical Utility Services to be disposed as an unopposed petition.

Upon review, the Commission finds that the PPL Electric’s LON and manner in which it was filed conform to the Commission’s regulations of 52 Pa. Code 57.72(d)(1)(vi) because the length of the transmission line to be constructed as part of the project is less than two miles.  Also the project is necessary to meet the increasing demand for electricity and improve reliability of service in the Tobyhanna Township area of Monroe County.  Above all, the Commission has reviewed the filing and finds it to be consistent with applicable law or Commission policy regarding transmission line siting.  Also, PPL Electric’s Zoning Petition and manner in which it was filed conform to the requirements of 52 Pa. Code §5.41 and 53 P.S. §10619.  PPL Electric has persuasively stated its case for the grant of its Petition and there was no protest to the Petition.  We recommend that the Application be approved and the Petition be granted; THEREFORE,

IT IS ORDERED:

# 1. That the Application filed by PPL Electric Utilities Corporation for the siting and construction of the Long Pond #1 and #2 138/69 kV Transmission Tap Line in Tobyhanna Township, Monroe County, Pennsylvania is hereby approved.

# 2. That the Petition of PPL Electric Utilities Corporation, pursuant to Section 619 of the MPC Act, for a finding that a building to shelter control equipment at the proposed Long Pond 69-12 kV Substation in Tobyhanna Township, Monroe County, Pennsylvania is reasonably necessary for the convenience or welfare of the public and, therefore exempt from any local zoning ordinance, is hereby granted.

# 3.	That this proceeding at Docket Nos. A-2013-2347931 and P-2013-2347936 be closed.

BY THE COMMISSION,

# Rosemary Chiavetta

Secretary

(SEAL)

# ORDER ADOPTED: July 16, 2013

# ORDER ENTERED: July 16, 2013

Kcmil is one thousand circular mils. A circular mil is the cross-sectional area of a wire one mil in diameter, where

1kcmil = 0.5067 mm2.

PPL Electric believes its control equipment building is not a "building" but, rather, is part of its substation facilities. Therefore, PPL Electric's control equipment building is exempt from local zoning requirements. See, e.g., Duquesne Light Co. v. Upper St. Clair Township, 377 Pa. 323, 334-35, 105 A.2d 287, 292 (1954). This Zoning Petition is being filed as a precaution in the event that the Commission were to determine that the control equipment building is not a facility and, therefore, potentially subject to local zoning ordinances.