## Manual
Pennsylvania Act 129 Motor & VFD Audit and Design Tool
MANUAL
Table of Contents:
I. Purpose
II. Organization
III. User Guide
IV. Disclaimer
I. Purpose
The purpose of the Motor & VFD Audit and Design Tool is two-fold:
1. To document the pre- and post-installation cases.
2. To facilitate the calculation of energy savings and demand reduction for motor and VFD installations.
II. Organization
The Motor & VFD Audit and Design Tool is organized into 6 sheets.
(1) Manual
The "Manual" sheet contains the instruction manual for using the Motor & VFD Audit and Design Tool.
(2) Changelog
The "Changelog" sheet provides a brief description of major changes from the previous version.
(3) Motor Form
The "Motor Form" sheet collects all relevant information to calculate energy savings and peak demand reduction for Motors. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. Note that the requirements of Section 3.3 (Premium Efficiency Motors) in the 2013 TRM restricts the protocol to only motor replacements without VFDs. This form must be used to calculate savings for motor replacement measures only (i.e. replacement of old motors with new energy efficient motors of the same rated horsepower).
The baseline motor and configuration details should be entered in the "Pre-Installation Data" section (rows 8-25) with no VFD, and the energy efficient motor and configuration details should be entered in the "Post-Installation Data" section (rows 26-42) with no VFD. The energy and peak demand savings resulting from the motor replacement alone will be automatically calculated in cells D45 and D46 respectively. To find out how to calculate savings resulting from VFD measures, refer to the notes described below.
(3) VFD Form
The "VFD Form" sheet collects all relevant information to calculate energy savings and peak demand reduction for VFDs. This form follows the conventions and equations described in the PA TRM and facilitates the calculation of gross energy savings for evaluation purposes. This form must be used to calculate savings for VFD measures only, not the combination of new motors and VSDs.
The motor and configuration details should be entered in the "VFD Installation Data" section (rows 10-24) for a motor with VFD. Select "Yes" for a VFD in Column N and select the baseline configuration details from the pull down menu. The ESF and DSF values are automatically populated in columbs P and Q. The energy and peak demand savings resulting from installation of VFD alone will be automatically calculated in cells D28 and D29 respectively. Note that custom protocols must be followed if the existing motor already has a VFD installed or if the VFD Baseline is not listed in the options.
(4) Summary
The "Summary" sheet summarizes the energy and peak demand savings for the entire project based on the calculations in "Motor Form" and "VFD Form" sheets.
a) Use the "Motor Form" to calculate savings resulting from Motor replacements only.
b) Use the "VFD Form" to calculate savings resulting from VFD installation only either on existing motor or energy efficient motor.
c) Add savings from the "Motor Form" and "VFD Form" sheets for projects with combination of both (VFDs and motor replacement).
(4) Glossary
The "Glossary" sheet is a reference for the "Motor and VFD Form" sheet. It defines each of the columns for clarification.
III. User Guide
The tool contains all information regarding motors and VFDs required for the calculation of savings pursuant to the PA TRM. The use of this tool is encouraged but not required. Users of the Motor and VFD Audit and Design Tool must complete the "Motor Form" and "VFD Form" depending on the measures installed for the project. For VFD measures in conjunction with a motor replacement measure, the savings must be calcualted separately using the "Motor Form" and "VFD Form". To find out how to calculate savings resulting from motor replacement and VFD measures separately, refer to the notes described above. The designer must select the appropriate facility type, utility, and program year from the drop down menu. Use one line on the pre-installation table and post-installation table for each unique motor, i.e. motors with different operating conditions or different motor specifications. Complete all yellow fields to calculate the peak demand reduction and annual energy savings. Pink fields are computed automatically. Roll mouse over the field heading for additional help. Projects within facility types or motor functions not included on the drop down menu must follow custom protocols to determine appropriate run hours and ESF/DSF values. Motor replacements with the following conditions should also follow custom protocols:
* Variable frequency drive (VFD) control on the existing (baseline) motor
* Two-speed motor (existing and/or new)
* Single speed motor with variable loading (not standard)
* Abnormal motor loading (i.e., load factor differs from 0.75)
* Industrial process applications
* Applications where the building type or motor usage group is not listed in Table 3-17 of the 2014 TRM
* New motor has a different rated horsepower than the existing motor
* Change in annual operating hours is anticipated
IV. Disclaimer
This document does not modify any requirements of the PA TRM and is provided for convenience only. If any discrepancy between the TRM and this document exist, the TRM should be followed.

## Changelog
Pennsylvania Act 129 Lighting Audit and Design Tool
CHANGELOG
Version 7 (Effective June 3, 2010)
1) | Released with TRM Order in June 2010
Version 8 (Submitted October 27, 2011. Effective June 1, 2011)
1) | Created Changelog
2) | Revised "Manual" and "Glossary" to improve user guide and increase usability
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM
Version 9 (Submitted September 13, 2011 for 2012 TRM Tentative Order)
1) | In "Motor and VFD Form", revised formulas in Columns O, P, and S to correct referencing errors
2) | In "Motor and VFD Form", added Column Q (Full Load kW) to correct a calculation error incorrectly applying DSF
3) | In "Motor and VFD Form", revised Column G (Coincidence Factor) to reflect TRM values (0.74 for single, 0.37 for duplex)
4) | In "Glossary", revised definition of coincidence factor to reflect above change.
5) | In "Glossary", added definition for "Full Load kW"
6) | In "Glossary", revised definition of "Nominal Efficiency" to reflect ability to custom input efficiency values for the new motor efficiency and baseline motor efficiency if the new motor is for new construction or replace on burnout.
7) | In "Manual", updated TRM reference from Table 6-12 to Table 3-15
Version 10 (Submitted December 5, 2011 for 2012 TRM Final Order)
1) | In "Motor and VFD Form", updated operating hours lookup table to reflect TRM table.
2) | In "Motor and VFD Form", corrected formulas for efficiency lookups, post-installation peak kW calculation, and total kWh calculation for post-installation line item #7.
3) | In "Motor and VFD Form", updated form to include new ESF and DSF values.
4) | In "Glossary", updated entries to reflect new column O and definition of "baseline".
Version 11 (Submitted August 31, 2012 for 2013 TRM Tentative Order)
1) | Created "Motor Form" and "VFD Form" to calculate savings for motors and VFD measures separately to be consistent with TRM protocols.
2) | In "Motor Form" and "VFD Form", updated operating hours lookup table to reflect TRM table.
3) | In "VFD Form", updated ESF and DSF values lookup table to reflect TRM table.
3) | Revised "Manual" and "Glossary" to reflect new changes to the TRM and Appendix D
Version 12 (Submitted December 07, 2012 for 2013 TRM Final Order)
1) | Changed the definition of "Load Factor" in Glossary to be consistent with TRM protocols.
Version 13 (Submitted August 29, 2013 for 2014 TRM Tentative Order)
1) | Revised the algorithms in Column R of the "VFD Form" tab used to calculate energy and peak demand savings to be consistent with TRM protocols. Removed a conversion factor of 0.746 to convert from HP to kW.

## Motor Form
Motor Inventory Form | [8 empty] | Appendix D of the PA TRM |  | Complete one copy of this form for each building with a motor measure
Applicant Name: | [6 empty] | Project Name:
Facility Name: | [6 empty] | Survey completed by (name):
Facility Type: | [6 empty] | Spot Measurements completed by (name):
Utility: | [6 empty] | Date(s) Survey completed:
Installation Date: | [6 empty] | Program Year:
Pre-Installation Data (Equipment Survey of Existing Motors)
[7 empty] | Nameplate Data | [5 empty] | Pre-Installation Energy Consumption
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Motor Configuration | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | Total per Unit |  |  |  | Total all Units
[13 empty] | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh |  | EPAct Efficiency | [6 empty] | NEMA Premium Efficiency | [6 empty] | Main Lookup Table |  |  |  | Efficiency Look Up
ex. | CWP-1 | CWP | 2 | 0.75 | Single | 0.74 | Acme | 10000 | 50 | 1800 | ODP | 93% | 30.1 | 22.3 | 1610 | 48430 | 44.5 | 96860 | Motor Functions | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | Facility | Motor Function | Concatenate | Run Hours | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600
[19 empty] | FM | 1 | 80% | 82.5% | 75.5% | 80% | 82.5% | 75.5% | 1 | 82.5% | 85.5% | 77% | 82.5% | 85.5% | 77% | Auto Related | FM | Auto Related FM | 4056 | 1 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
1 | [18 empty] | CHWP/CTF | 1.5 | 84% | 84% | 82.5% | 85.5% | 84% | 82.5% | 1.5 | 86.5% | 86.5% | 84% | 87.5% | 86.5% | 84% | Auto Related | CHWP/CTF | Auto Related CHWP/CTF | 1878 | 1.5 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
2 | [18 empty] | HWP | 2 | 85.5% | 84% | 84% | 86.5% | 84% | 84% | 2 | 87.5% | 86.5% | 85.5% | 88.5% | 86.5% | 85.5% | Auto Related | HWP | Auto Related HWP | 6000 | 2 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
3 | [19 empty] | 3 | 86.5% | 86.5% | 84% | 87.5% | 87.5% | 85.5% | 3 | 88.5% | 89.5% | 85.5% | 89.5% | 89.5% | 86.5% | Bakery | FM | BakeryFM | 2854 | 3 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
4 | [18 empty] | Utility | 5 | 87.5% | 87.5% | 85.5% | 87.5% | 87.5% | 87.5% | 5 | 89.5% | 89.5% | 86.5% | 89.5% | 89.5% | 88.5% | Bakery | CHWP/CTF | BakeryCHWP/CTF | 1445 | 5 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
5 | [18 empty] | Duquesne Light | 7.5 | 88.5% | 88.5% | 87.5% | 89.5% | 89.5% | 88.5% | 7.5 | 90.2% | 91% | 88.5% | 91% | 91.7% | 89.5% | Bakery | HWP | BakeryHWP | 6000 | 7.5 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
6 | [18 empty] | Met-Ed (FirstEnergy) | 10 | 90.2% | 89.5% | 88.5% | 89.5% | 89.5% | 89.5% | 10 | 91.7% | 91.7% | 89.5% | 91% | 91.7% | 90.2% | Banks, Financial Centers | FM | Banks, Financial Centers FM | 3748 | 10 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
7 | [18 empty] | Penn Power (FirstEnergy) | 15 | 90.2% | 91% | 89.5% | 90.2% | 91% | 90.2% | 15 | 91.7% | 93% | 90.2% | 91.7% | 92.4% | 91% | Banks, Financial Centers | CHWP/CTF | Banks, Financial Centers CHWP/CTF | 1767 | 15 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
8 | [18 empty] | PennElec (FirstEnergy) | 20 | 91% | 91% | 90.2% | 90.2% | 91% | 90.2% | 20 | 92.4% | 93% | 91% | 91.7% | 93% | 91% | Banks, Financial Centers | HWP | Banks, Financial Centers HWP | 6000 | 20 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
9 | [18 empty] | West Penn Power (FirstEnergy) | 25 | 91.7% | 91.7% | 91% | 91.7% | 92.4% | 91% | 25 | 93% | 93.6% | 91.7% | 93% | 93.6% | 91.7% | Church | FM | Church FM | 1955 | 25 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
10 | [18 empty] | PECO | 30 | 92.4% | 92.4% | 91% | 91.7% | 92.4% | 91% | 30 | 93.6% | 94.1% | 91.7% | 93% | 93.6% | 91.7% | Church | CHWP/CTF | Church CHWP/CTF | 1121 | 30 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[17 empty] | 0 | 0 | PPL | 40 | 93% | 93% | 91.7% | 93% | 93% | 91.7% | 40 | 94.1% | 94.1% | 92.4% | 94.1% | 94.1% | 92.4% | Church | HWP | Church HWP | 6000 | 40 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
Post-Installation Data (Equipment Survey of Proposed Motors) | [19 empty] | 50 | 93% | 93% | 92.4% | 93% | 93% | 92.4% | 50 | 94.1% | 94.5% | 93% | 94.1% | 94.5% | 93% | College – Cafeteria | FM | College – Cafeteria FM | 6376 | 50 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[7 empty] | Nameplate Data | [5 empty] | Post-Installation Energy Consumption | [5 empty] | Facility Types | 60 | 93.6% | 93.6% | 93% | 93.6% | 93.6% | 93% | 60 | 94.5% | 95% | 93.6% | 94.5% | 95% | 93.6% | College – Cafeteria | CHWP/CTF | College – Cafeteria CHWP/CTF | 2713 | 60 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Motor Configuration | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | Total per Unit |  |  |  | Total all Units |  | Auto Related | 75 | 93.6% | 94.1% | 93% | 93.6% | 94.1% | 93% | 75 | 94.5% | 95% | 93.6% | 94.5% | 95.4% | 93.6% | College – Cafeteria | HWP | College – Cafeteria HWP | 6000 | 75 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[13 empty] | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh | Bakery | 100 | 94.1% | 94.1% | 93% | 94.1% | 94.5% | 93.6% | 100 | 95% | 95.4% | 93.6% | 95% | 95.4% | 94.1% | College - Classes/Administrative | FM | College - Classes/Administrative FM | 2586 | 100 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[19 empty] | Banks, Financial Centers | 125 | 94.1% | 94.5% | 93.6% | 94.1% | 94.5% | 94.5% | 125 | 95% | 95.4% | 94.1% | 95% | 95.4% | 95% | College - Classes/Administrative | CHWP/CTF | College - Classes/Administrative CHWP/CTF | 1348 | 125 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
ex. | CWP-1 | CWP | 2 | 0.75 | Single | 0.74 | Acme | 20000 | 50 | 1800 | ODP | 94.5% | 29.6 | 21.9 | 1610 | 47660 | 43.8 | 95322 | Church | 150 | 94.5% | 95% | 93.6% | 95% | 95% | 94.5% | 150 | 95.4% | 95.8% | 94.1% | 95.8% | 95.8% | 95% | College - Classes/Administrative | HWP | College - Classes/Administrative HWP | 6000 | 150 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[19 empty] | College – Cafeteria | 200 | 94.5% | 95% | 94.5% | 95% | 95% | 95% | 200 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.4% | College - Dormitory | FM | College - Dormitory FM | 3066 | 200 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
1 | [18 empty] | College - Classes/Administrative | 250 | N/A | N/A | N/A | N/A | N/A | N/A | 250 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.8% | College - Dormitory | CHWP/CTF | College - Dormitory CHWP/CTF | 1521 | 250 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
2 | [18 empty] | College - Dormitory | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | 95.4% | 95.8% | 95.4% | 95.8% | 96.2% | 95.8% | College - Dormitory | HWP | College - Dormitory HWP | 6000 | 300 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
3 | [18 empty] | Commercial Condos | 350 | N/A | N/A | N/A | N/A | N/A | N/A | 350 | 95.4% | 95.8% | 95.4% | 95.8% | 96.2% | 95.8% | Commercial Condos | FM | Commercial Condos FM | 4055 | 350 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
4 | [18 empty] | Convenience Stores | 400 | N/A | N/A | N/A | N/A | N/A | N/A | 400 | 95.8% | 95.8% | 95.8% | 95.8% | 96.2% | 95.8% | Commercial Condos | CHWP/CTF | Commercial Condos CHWP/CTF | 1877 | 400 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
5 | [18 empty] | Convention Center | 450 | N/A | N/A | N/A | N/A | N/A | N/A | 450 | 96.2% | 96.2% | 95.8% | 95.8% | 96.2% | 95.8% | Commercial Condos | HWP | Commercial Condos HWP | 6000 | 450 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
6 | [18 empty] | Court House | 500 | N/A | N/A | N/A | N/A | N/A | N/A | 500 | 96.2% | 96.2% | 95.8% | 95.8% | 96.2% | 95.8% | Convenience Stores | FM | Convenience Stores FM | 6376 | 500 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
7 | [18 empty] | Dining: Bar Lounge/Leisure | [14 empty] | Convenience Stores | CHWP/CTF | Convenience Stores CHWP/CTF | 2713
8 | [18 empty] | Dining: Cafeteria / Fast Food | [14 empty] | Convenience Stores | HWP | Convenience Stores HWP | 6000
9 | [18 empty] | Dining: Family | [14 empty] | Convention Center | FM | Convention Center FM | 1954
10 | [18 empty] | Entertainment | [14 empty] | Convention Center | CHWP/CTF | Convention Center CHWP/CTF | 1121
[17 empty] | 0 | 0 | Exercise Center | [14 empty] | Convention Center | HWP | Convention Center HWP | 6000
Savings Data | [18 empty] | Fast Food Restaurants | [14 empty] | Court House | FM | Court House FM | 3748
Total Peak kW Reduction |  |  | 0 | [15 empty] | Fire Station (Unmanned) | [14 empty] | Court House | CHWP/CTF | Court House CHWP/CTF | 1767
Total Annual kWh Savings |  |  | 0 | [15 empty] | Food Stores | [14 empty] | Court House | HWP | Court House HWP | 6000
[19 empty] | Gymnasium | [14 empty] | Dining: Bar Lounge/Leisure | FM | Dining: Bar Lounge/Leisure FM | 4182
[19 empty] | Hospitals | [14 empty] | Dining: Bar Lounge/Leisure | CHWP/CTF | Dining: Bar Lounge/Leisure CHWP/CTF | 1923
[19 empty] | Hospitals / Health Care | [14 empty] | Dining: Bar Lounge/Leisure | HWP | Dining: Bar Lounge/Leisure HWP | 6000
[19 empty] | Industrial - 1 Shift | [14 empty] | Dining: Cafeteria / Fast Food | FM | Dining: Cafeteria / Fast Food FM | 6456
[19 empty] | Industrial - 2 Shift | [14 empty] | Dining: Cafeteria / Fast Food | CHWP/CTF | Dining: Cafeteria / Fast Food CHWP/CTF | 2742
[19 empty] | Industrial - 3 Shift | [14 empty] | Dining: Cafeteria / Fast Food | HWP | Dining: Cafeteria / Fast Food HWP | 6000
[19 empty] | Laundromats | [14 empty] | Dining: Family | FM | Dining: Family FM | 4182
[19 empty] | Library | [14 empty] | Dining: Family | CHWP/CTF | Dining: Family CHWP/CTF | 1923
[19 empty] | Light Manufacturers | [14 empty] | Dining: Family | HWP | Dining: Family HWP | 6000
[19 empty] | Lodging (Hotels/Motels) | [14 empty] | Entertainment | FM | EntertainmentFM | 1952
[19 empty] | Mall Concourse | [14 empty] | Entertainment | CHWP/CTF | EntertainmentCHWP/CTF | 1120
[19 empty] | Manufacturing Facility | [14 empty] | Entertainment | HWP | EntertainmentHWP | 6000
[19 empty] | Medical Offices | [14 empty] | Exercise Center | FM | Exercise Center FM | 5836
[19 empty] | Motion Picture Theatre | [14 empty] | Exercise Center | CHWP/CTF | Exercise Center CHWP/CTF | 2518
[19 empty] | Multi-Family (Common Areas) | [14 empty] | Exercise Center | HWP | Exercise Center HWP | 6000
[19 empty] | Museum | [14 empty] | Fast Food Restaurants | FM | Fast Food Restaurants FM | 6376
[19 empty] | Nursing Homes | [14 empty] | Fast Food Restaurants | CHWP/CTF | Fast Food Restaurants CHWP/CTF | 2713
[19 empty] | Office (General Office Types) | [14 empty] | Fast Food Restaurants | HWP | Fast Food Restaurants HWP | 6000
[19 empty] | Office/Retail | [14 empty] | Fire Station (Unmanned) | FM | Fire Station (Unmanned) FM | 1953
[19 empty] | Parking Garages & Lots | [14 empty] | Fire Station (Unmanned) | CHWP/CTF | Fire Station (Unmanned) CHWP/CTF | 1121
[19 empty] | Penitentiary | [14 empty] | Fire Station (Unmanned) | HWP | Fire Station (Unmanned) HWP | 6000
[19 empty] | Performing Arts Theatre | [14 empty] | Food Stores | FM | Food Stores FM | 4055
[19 empty] | Police / Fire Stations (24 Hr) | [14 empty] | Food Stores | CHWP/CTF | Food Stores CHWP/CTF | 1877
[19 empty] | Post Office | [14 empty] | Food Stores | HWP | Food Stores HWP | 6000
[19 empty] | Pump Stations | [14 empty] | Gymnasium | FM | GymnasiumFM | 2586
[19 empty] | Refrigerated Warehouse | [14 empty] | Gymnasium | CHWP/CTF | GymnasiumCHWP/CTF | 1348
[19 empty] | Religious Building | [14 empty] | Gymnasium | HWP | GymnasiumHWP | 6000
[19 empty] | Residential (Except Nursing Homes) | [14 empty] | Hospitals | FM | HospitalsFM | 7674
[19 empty] | Restaurants | [14 empty] | Hospitals | CHWP/CTF | HospitalsCHWP/CTF | 3180
[19 empty] | Retail | [14 empty] | Hospitals | HWP | HospitalsHWP | 6000
[19 empty] | School / University | [14 empty] | Hospitals / Health Care | FM | Hospitals / Health Care FM | 7666
[19 empty] | Schools (Jr./Sr. High) | [14 empty] | Hospitals / Health Care | CHWP/CTF | Hospitals / Health Care CHWP/CTF | 3177
[19 empty] | Schools (Preschool/Elementary) | [14 empty] | Hospitals / Health Care | HWP | Hospitals / Health Care HWP | 6000
[19 empty] | Schools (Technical/Vocational) | [14 empty] | Industrial - 1 Shift | FM | Industrial - 1 Shift FM | 2857
[19 empty] | Small Services | [14 empty] | Industrial - 1 Shift | CHWP/CTF | Industrial - 1 Shift CHWP/CTF | 1446
[19 empty] | Sports Arena | [14 empty] | Industrial - 1 Shift | HWP | Industrial - 1 Shift HWP | 6000
[19 empty] | Town Hall | [14 empty] | Industrial - 2 Shift | FM | Industrial - 2 Shift FM | 4730
[19 empty] | Transportation | [14 empty] | Industrial - 2 Shift | CHWP/CTF | Industrial - 2 Shift CHWP/CTF | 2120
[19 empty] | Warehouse (Not Refrigerated) | [14 empty] | Industrial - 2 Shift | HWP | Industrial - 2 Shift HWP | 6000
[19 empty] | Waste Water Treatment Plant | [14 empty] | Industrial - 3 Shift | FM | Industrial - 3 Shift FM | 6631
[19 empty] | Workshop | [14 empty] | Industrial - 3 Shift | CHWP/CTF | Industrial - 3 Shift CHWP/CTF | 2805
[19 empty] | Other | [14 empty] | Industrial - 3 Shift | HWP | Industrial - 3 Shift HWP | 6000
[34 empty] | Laundromats | FM | Laundromats FM | 4056
[34 empty] | Laundromats | CHWP/CTF | Laundromats CHWP/CTF | 1878
[19 empty] | Program Years in Phase II | [14 empty] | Laundromats | HWP | Laundromats HWP | 6000
[19 empty] | Program Year 5 | [14 empty] | Library | FM | LibraryFM | 3748
[19 empty] | Program Year 6 | [14 empty] | Library | CHWP/CTF | LibraryCHWP/CTF | 1767
[19 empty] | Program Year 7 | [14 empty] | Library | HWP | LibraryHWP | 6000
[34 empty] | Light Manufacturers | FM | Light Manufacturers FM | 2857
[34 empty] | Light Manufacturers | CHWP/CTF | Light Manufacturers CHWP/CTF | 1446
[34 empty] | Light Manufacturers | HWP | Light Manufacturers HWP | 6000
[34 empty] | Lodging (Hotels/Motels) | FM | Lodging (Hotels/Motels) FM | 3064
[34 empty] | Lodging (Hotels/Motels) | CHWP/CTF | Lodging (Hotels/Motels) CHWP/CTF | 1521
[34 empty] | Lodging (Hotels/Motels) | HWP | Lodging (Hotels/Motels) HWP | 6000
[34 empty] | Mall Concourse | FM | Mall Concourse FM | 4833
[34 empty] | Mall Concourse | CHWP/CTF | Mall Concourse CHWP/CTF | 2157
[34 empty] | Mall Concourse | HWP | Mall Concourse HWP | 6000
[34 empty] | Manufacturing Facility | FM | Manufacturing Facility FM | 2857
[34 empty] | Manufacturing Facility | CHWP/CTF | Manufacturing Facility CHWP/CTF | 1446
[34 empty] | Manufacturing Facility | HWP | Manufacturing Facility HWP | 6000
[34 empty] | Medical Offices | FM | Medical Offices FM | 3748
[34 empty] | Medical Offices | CHWP/CTF | Medical Offices CHWP/CTF | 1767
[34 empty] | Medical Offices | HWP | Medical Offices HWP | 6000
[34 empty] | Motion Picture Theatre | FM | Motion Picture Theatre FM | 1954
[34 empty] | Motion Picture Theatre | CHWP/CTF | Motion Picture Theatre CHWP/CTF | 1121
[34 empty] | Motion Picture Theatre | HWP | Motion Picture Theatre HWP | 6000
[34 empty] | Multi-Family (Common Areas) | FM | Multi-Family (Common Areas) FM | 7665
[34 empty] | Multi-Family (Common Areas) | CHWP/CTF | Multi-Family (Common Areas) CHWP/CTF | 3177
[34 empty] | Multi-Family (Common Areas) | HWP | Multi-Family (Common Areas) HWP | 6000
[34 empty] | Museum | FM | MuseumFM | 3748
[34 empty] | Museum | CHWP/CTF | MuseumCHWP/CTF | 1767
[34 empty] | Museum | HWP | MuseumHWP | 6000
[34 empty] | Nursing Homes | FM | Nursing Homes FM | 5840
[34 empty] | Nursing Homes | CHWP/CTF | Nursing Homes CHWP/CTF | 2520
[34 empty] | Nursing Homes | HWP | Nursing Homes HWP | 6000
[34 empty] | Office (General Office Types) | FM | Office (General Office Types) FM | 3748
[34 empty] | Office (General Office Types) | CHWP/CTF | Office (General Office Types) CHWP/CTF | 1767
[34 empty] | Office (General Office Types) | HWP | Office (General Office Types) HWP | 6000
[34 empty] | Office/Retail | FM | Office/RetailFM | 3748
[34 empty] | Office/Retail | CHWP/CTF | Office/RetailCHWP/CTF | 1767
[34 empty] | Office/Retail | HWP | Office/RetailHWP | 6000
[34 empty] | Parking Garages & Lots | FM | Parking Garages & Lots FM | 4368
[34 empty] | Parking Garages & Lots | CHWP/CTF | Parking Garages & Lots CHWP/CTF | 1990
[34 empty] | Parking Garages & Lots | HWP | Parking Garages & Lots HWP | 6000
[34 empty] | Penitentiary | FM | PenitentiaryFM | 5477
[34 empty] | Penitentiary | CHWP/CTF | PenitentiaryCHWP/CTF | 2389
[34 empty] | Penitentiary | HWP | PenitentiaryHWP | 6000
[34 empty] | Performing Arts Theatre | FM | Performing Arts Theatre FM | 2586
[34 empty] | Performing Arts Theatre | CHWP/CTF | Performing Arts Theatre CHWP/CTF | 1348
[34 empty] | Performing Arts Theatre | HWP | Performing Arts Theatre HWP | 6000
[34 empty] | Police / Fire Stations (24 Hr) | FM | Police / Fire Stations (24 Hr) FM | 7665
[34 empty] | Police / Fire Stations (24 Hr) | CHWP/CTF | Police / Fire Stations (24 Hr) CHWP/CTF | 3177
[34 empty] | Police / Fire Stations (24 Hr) | HWP | Police / Fire Stations (24 Hr) HWP | 6000
[34 empty] | Post Office | FM | Post Office FM | 3748
[34 empty] | Post Office | CHWP/CTF | Post Office CHWP/CTF | 1767
[34 empty] | Post Office | HWP | Post Office HWP | 6000
[34 empty] | Pump Stations | FM | Pump Stations FM | 1949
[34 empty] | Pump Stations | CHWP/CTF | Pump Stations CHWP/CTF | 1119
[34 empty] | Pump Stations | HWP | Pump Stations HWP | 6000
[34 empty] | Refrigerated Warehouse | FM | Refrigerated Warehouse FM | 2602
[34 empty] | Refrigerated Warehouse | CHWP/CTF | Refrigerated Warehouse CHWP/CTF | 1354
[34 empty] | Refrigerated Warehouse | HWP | Refrigerated Warehouse HWP | 6000
[34 empty] | Religious Building | FM | Religious Building FM | 1955
[34 empty] | Religious Building | CHWP/CTF | Religious Building CHWP/CTF | 1121
[34 empty] | Religious Building | HWP | Religious Building HWP | 6000
[34 empty] | Residential (Except Nursing Homes) | FM | Residential (Except Nursing Homes) FM | 3066
[34 empty] | Residential (Except Nursing Homes) | CHWP/CTF | Residential (Except Nursing Homes) CHWP/CTF | 1521
[34 empty] | Residential (Except Nursing Homes) | HWP | Residential (Except Nursing Homes) HWP | 6000
[34 empty] | Restaurants | FM | Restaurants FM | 4182
[34 empty] | Restaurants | CHWP/CTF | Restaurants CHWP/CTF | 1923
[34 empty] | Restaurants | HWP | Restaurants HWP | 6000
[34 empty] | Retail | FM | RetailFM | 4057
[34 empty] | Retail | CHWP/CTF | RetailCHWP/CTF | 1878
[34 empty] | Retail | HWP | RetailHWP | 6000
[34 empty] | School / University | FM | School / University FM | 2187
[34 empty] | School / University | CHWP/CTF | School / University CHWP/CTF | 1205
[34 empty] | School / University | HWP | School / University HWP | 6000
[34 empty] | Schools (Jr./Sr. High) | FM | Schools (Jr./Sr. High) FM | 2187
[34 empty] | Schools (Jr./Sr. High) | CHWP/CTF | Schools (Jr./Sr. High) CHWP/CTF | 1205
[34 empty] | Schools (Jr./Sr. High) | HWP | Schools (Jr./Sr. High) HWP | 6000
[34 empty] | Schools (Preschool/Elementary) | FM | Schools (Preschool/Elementary) FM | 2187
[34 empty] | Schools (Preschool/Elementary) | CHWP/CTF | Schools (Preschool/Elementary) CHWP/CTF | 1205
[34 empty] | Schools (Preschool/Elementary) | HWP | Schools (Preschool/Elementary) HWP | 6000
[34 empty] | Schools (Technical/Vocational) | FM | Schools (Technical/Vocational) FM | 2187
[34 empty] | Schools (Technical/Vocational) | CHWP/CTF | Schools (Technical/Vocational) CHWP/CTF | 1205
[34 empty] | Schools (Technical/Vocational) | HWP | Schools (Technical/Vocational) HWP | 6000
[34 empty] | Small Services | FM | Small Services FM | 3750
[34 empty] | Small Services | CHWP/CTF | Small Services CHWP/CTF | 1768
[34 empty] | Small Services | HWP | Small Services HWP | 6000
[34 empty] | Sports Arena | FM | Sports Arena FM | 1954
[34 empty] | Sports Arena | CHWP/CTF | Sports Arena CHWP/CTF | 1121
[34 empty] | Sports Arena | HWP | Sports Arena HWP | 6000
[34 empty] | Town Hall | FM | Town Hall FM | 3748
[34 empty] | Town Hall | CHWP/CTF | Town Hall CHWP/CTF | 1767
[34 empty] | Town Hall | HWP | Town Hall HWP | 6000
[34 empty] | Transportation | FM | TransportationFM | 6456
[34 empty] | Transportation | CHWP/CTF | TransportationCHWP/CTF | 2742
[34 empty] | Transportation | HWP | TransportationHWP | 6000
[34 empty] | Warehouse (Not Refrigerated) | FM | Warehouse (Not Refrigerated) FM | 2602
[34 empty] | Warehouse (Not Refrigerated) | CHWP/CTF | Warehouse (Not Refrigerated) CHWP/CTF | 1354
[34 empty] | Warehouse (Not Refrigerated) | HWP | Warehouse (Not Refrigerated) HWP | 6000
[34 empty] | Waste Water Treatment Plant | FM | Waste Water Treatment Plant FM | 6631
[34 empty] | Waste Water Treatment Plant | CHWP/CTF | Waste Water Treatment Plant CHWP/CTF | 2805
[34 empty] | Waste Water Treatment Plant | HWP | Waste Water Treatment Plant HWP | 6000
[34 empty] | Workshop | FM | Workshop FM | 3750
[34 empty] | Workshop | CHWP/CTF | Workshop CHWP/CTF | 1768
[34 empty] | Workshop | HWP | Workshop HWP | 6000
[34 empty] | Other | FM | OtherFM | 3985
[34 empty] | Other | CHWP/CTF | OtherCHWP/CTF | 1852
[34 empty] | Other | HWP | OtherHWP | 6000
Note on C10: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours for motor functions not listed. FM: Fan Motor CHWP/CTF: Chilled Water Pump/ Cooling Tower Fan HWP: Heating Hot Water Pump
Note on K10: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on M10: Nominal Efficiency Select Motor Horsepower, Synchronous Speed and Enclosure Type to determine nominal efficiency.
Note on E10: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on J10: Motor Horsepower Select the rated horsepower of the motor.
Note on L10: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on B10: Unique Motor I.D. Provide designation to identify the motor(s).
Note on F10: Motor Configuration Select the appropriate motor configuration. If the motor configuration is not listed, a custom motor protocol must be used. Single: One motor serving the load. Duplex: Two motors serving the load, one as standby.
Note on H10: Manufacturer Provide the motor manufacturer's name.
Note on I10: Model Number Provide the motor model number.
Note on C4: Facility Type Select the appropriate facility type from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours, Coincidence Factors, ESF and DSF (as applicable) for building types not listed.
Note on C5: Utility Select the utility serving the facility from the pull down menu.
Note on B28: Unique Motor I.D. Provide designation to identify the motor(s).
Note on F28: Motor Configuration Motors can be set up in different configurations; individually, in parallel, in lead-lag. Select the most appropriate configuration for the motor(s).
Note on H28: Manufacturer Provide the motor manufacturer's name.
Note on I28: Model Number Provide the motor model number.
Note on J28: Motor Horsepower Select the rated horsepower of the motor.
Note on K28: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on L28: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on D10: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on M28: Nominal Efficiency Input nominal efficiency from the motor nameplate
Note on E28: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on K6: Program Year: Program Year 5: June 1, 2013 - May 31, 2014 Program Year 6: June 1, 2014 - May 31, 2015 Program Year 7: June 1, 2015 - May 31, 2016
Note on D28: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on C28: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours for motor functions not listed. FM: Fan Motor CHWP/CTF: Chilled Water Pump/ Cooling Tower Fan HWP: Heating Hot Water Pump

## VFD Form
Variable Frequency Drive Inventory Form | [8 empty] | Appendix D of the PA TRM |  | Complete one copy of this form for each building with a VFD measure
Applicant Name: | [6 empty] | Project Name:
Facility Name: | [6 empty] | Survey completed by (name):
Facility Type: | [6 empty] | Spot Measurements completed by (name):
Utility: | [6 empty] | Date(s) Survey completed:
Installation Date: | [6 empty] | Program Year:
VFD Installation Data (Equipment Survey of Existing or Proposed Motors)
[7 empty] | Nameplate Data | [5 empty] | Pre-Installation Energy Consumption
Line Item | Unique Motor I.D.(s) | Motor Function | Number of Identical Units | Load Factor (LF) | Motor Configuration | Coincidence Factor (CF) | Manufacturer | Model Number | Motor Horsepower | Synchronous Speed (RPM) | Enclosure Type | Nominal Efficiency | VFD |  |  |  | Total Savings per Unit |  |  |  | Total Savings all Units
[13 empty] | VFD on Motor | Baseline | ESF | DSF | Full Load kW | Peak kW | Operating Hours | Annual kWh | Peak kW | Annual kWh |  | EPAct Efficiency | [6 empty] | NEMA Premium Efficiency | [6 empty] | Main Lookup Table |  |  |  | Efficiency Look Up | [6 empty] | ESF & DSF Look Up
ex. | CWP-1 | CWP | 2 | 0.75 | Single | 0.74 | Acme | 10000 | 50 | 1800 | ODP | 93% | Yes | AFBI | 0.354 | 0.26 | 40.3 | 7.8 | 1610 | 22981 | 15.5 | 45963 | Utility | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | Facility | Motor Function | Concatenate | Run Hours | HP | ODP1200 | ODP1800 | ODP3600 | TEFC1200 | TEFC1800 | TEFC3600 | Type | Abrv | ESF | DSF
[23 empty] | Duquesne Light | 1 | 80% | 82.5% | 75.5% | 80% | 82.5% | 75.5% | 1 | 82.5% | 85.5% | 77% | 82.5% | 85.5% | 77% | Auto Related | FM | Auto Related FM | 4056 | 1 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | None | N/A | 0 | 0
1 | [22 empty] | Met-Ed (FirstEnergy) | 1.5 | 84% | 84% | 82.5% | 85.5% | 84% | 82.5% | 1.5 | 86.5% | 86.5% | 84% | 87.5% | 86.5% | 84% | Auto Related | CHWP/CTF | Auto Related CHWP/CTF | 1878 | 1.5 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Constant Volume | CV | 0.534 | 0.347
2 | [22 empty] | Penn Power (FirstEnergy) | 2 | 85.5% | 84% | 84% | 86.5% | 84% | 84% | 2 | 87.5% | 86.5% | 85.5% | 88.5% | 86.5% | 85.5% | Auto Related | HWP | Auto Related HWP | 6000 | 2 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Air Foil/Backward Incline | AFBI | 0.354 | 0.26
3 | [22 empty] | PennElec (FirstEnergy) | 3 | 86.5% | 86.5% | 84% | 87.5% | 87.5% | 85.5% | 3 | 88.5% | 89.5% | 85.5% | 89.5% | 89.5% | 86.5% | Bakery | FM | BakeryFM | 2854 | 3 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Air Foil/Backward Incline with Inlet Guide Vanes | AFBI IGV | 0.227 | 0.13
4 | [22 empty] | West Penn Power (FirstEnergy) | 5 | 87.5% | 87.5% | 85.5% | 87.5% | 87.5% | 87.5% | 5 | 89.5% | 89.5% | 86.5% | 89.5% | 89.5% | 88.5% | Bakery | CHWP/CTF | BakeryCHWP/CTF | 1445 | 5 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Forward Curved | FC | 0.179 | 0.136
5 | [22 empty] | PECO | 7.5 | 88.5% | 88.5% | 87.5% | 89.5% | 89.5% | 88.5% | 7.5 | 90.2% | 91% | 88.5% | 91% | 91.7% | 89.5% | Bakery | HWP | BakeryHWP | 6000 | 7.5 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Forward Curved with Inlet Guide Vanes | FC IGV | 0.092 | 0.029
6 | [22 empty] | PPL | 10 | 90.2% | 89.5% | 88.5% | 89.5% | 89.5% | 89.5% | 10 | 91.7% | 91.7% | 89.5% | 91% | 91.7% | 90.2% | Banks, Financial Centers | FM | Banks, Financial Centers FM | 3748 | 10 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Chilled Water Pump | CHWP | 0.411 | 0.299
7 | [23 empty] | 15 | 90.2% | 91% | 89.5% | 90.2% | 91% | 90.2% | 15 | 91.7% | 93% | 90.2% | 91.7% | 92.4% | 91% | Banks, Financial Centers | CHWP/CTF | Banks, Financial Centers CHWP/CTF | 1767 | 15 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY | Hot Water Pump | HWP | 0.424 | 0
8 | [23 empty] | 20 | 91% | 91% | 90.2% | 90.2% | 91% | 90.2% | 20 | 92.4% | 93% | 91% | 91.7% | 93% | 91% | Banks, Financial Centers | HWP | Banks, Financial Centers HWP | 6000 | 20 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
9 | [22 empty] | Motor Functions | 25 | 91.7% | 91.7% | 91% | 91.7% | 92.4% | 91% | 25 | 93% | 93.6% | 91.7% | 93% | 93.6% | 91.7% | Church | FM | Church FM | 1955 | 25 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
10 | [22 empty] | FM | 30 | 92.4% | 92.4% | 91% | 91.7% | 92.4% | 91% | 30 | 93.6% | 94.1% | 91.7% | 93% | 93.6% | 91.7% | Church | CHWP/CTF | Church CHWP/CTF | 1121 | 30 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[21 empty] | 0 | 0 | CHWP/CTF | 40 | 93% | 93% | 91.7% | 93% | 93% | 91.7% | 40 | 94.1% | 94.1% | 92.4% | 94.1% | 94.1% | 92.4% | Church | HWP | Church HWP | 6000 | 40 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | HWP | 50 | 93% | 93% | 92.4% | 93% | 93% | 92.4% | 50 | 94.1% | 94.5% | 93% | 94.1% | 94.5% | 93% | College – Cafeteria | FM | College – Cafeteria FM | 6376 | 50 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
Savings Data | [23 empty] | 60 | 93.6% | 93.6% | 93% | 93.6% | 93.6% | 93% | 60 | 94.5% | 95% | 93.6% | 94.5% | 95% | 93.6% | College – Cafeteria | CHWP/CTF | College – Cafeteria CHWP/CTF | 2713 | 60 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
Total Peak kW Reduction |  |  | 0 | [19 empty] | Facility Types | 75 | 93.6% | 94.1% | 93% | 93.6% | 94.1% | 93% | 75 | 94.5% | 95% | 93.6% | 94.5% | 95.4% | 93.6% | College – Cafeteria | HWP | College – Cafeteria HWP | 6000 | 75 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
Total Annual kWh Savings |  |  | 0 | [19 empty] | Auto Related | 100 | 94.1% | 94.1% | 93% | 94.1% | 94.5% | 93.6% | 100 | 95% | 95.4% | 93.6% | 95% | 95.4% | 94.1% | College - Classes/Administrative | FM | College - Classes/Administrative FM | 2586 | 100 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Bakery | 125 | 94.1% | 94.5% | 93.6% | 94.1% | 94.5% | 94.5% | 125 | 95% | 95.4% | 94.1% | 95% | 95.4% | 95% | College - Classes/Administrative | CHWP/CTF | College - Classes/Administrative CHWP/CTF | 1348 | 125 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Banks, Financial Centers | 150 | 94.5% | 95% | 93.6% | 95% | 95% | 94.5% | 150 | 95.4% | 95.8% | 94.1% | 95.8% | 95.8% | 95% | College - Classes/Administrative | HWP | College - Classes/Administrative HWP | 6000 | 150 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Church | 200 | 94.5% | 95% | 94.5% | 95% | 95% | 95% | 200 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.4% | College - Dormitory | FM | College - Dormitory FM | 3066 | 200 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | College – Cafeteria | 250 | N/A | N/A | N/A | N/A | N/A | N/A | 250 | 95.4% | 95.8% | 95% | 95.8% | 96.2% | 95.8% | College - Dormitory | CHWP/CTF | College - Dormitory CHWP/CTF | 1521 | 250 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | College - Classes/Administrative | 300 | N/A | N/A | N/A | N/A | N/A | N/A | 300 | 95.4% | 95.8% | 95.4% | 95.8% | 96.2% | 95.8% | College - Dormitory | HWP | College - Dormitory HWP | 6000 | 300 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | College - Dormitory | 350 | N/A | N/A | N/A | N/A | N/A | N/A | 350 | 95.4% | 95.8% | 95.4% | 95.8% | 96.2% | 95.8% | Commercial Condos | FM | Commercial Condos FM | 4055 | 350 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Commercial Condos | 400 | N/A | N/A | N/A | N/A | N/A | N/A | 400 | 95.8% | 95.8% | 95.8% | 95.8% | 96.2% | 95.8% | Commercial Condos | CHWP/CTF | Commercial Condos CHWP/CTF | 1877 | 400 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Convenience Stores | 450 | N/A | N/A | N/A | N/A | N/A | N/A | 450 | 96.2% | 96.2% | 95.8% | 95.8% | 96.2% | 95.8% | Commercial Condos | HWP | Commercial Condos HWP | 6000 | 450 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Convention Center | 500 | N/A | N/A | N/A | N/A | N/A | N/A | 500 | 96.2% | 96.2% | 95.8% | 95.8% | 96.2% | 95.8% | Convenience Stores | FM | Convenience Stores FM | 6376 | 500 | Select PY | Select PY | Select PY | Select PY | Select PY | Select PY
[23 empty] | Court House | [14 empty] | Convenience Stores | CHWP/CTF | Convenience Stores CHWP/CTF | 2713
[23 empty] | Dining: Bar Lounge/Leisure | [14 empty] | Convenience Stores | HWP | Convenience Stores HWP | 6000
[23 empty] | Dining: Cafeteria / Fast Food | [14 empty] | Convention Center | FM | Convention Center FM | 1954
[23 empty] | Dining: Family | [14 empty] | Convention Center | CHWP/CTF | Convention Center CHWP/CTF | 1121
[23 empty] | Entertainment | [14 empty] | Convention Center | HWP | Convention Center HWP | 6000
[23 empty] | Exercise Center | [14 empty] | Court House | FM | Court House FM | 3748
[23 empty] | Fast Food Restaurants | [14 empty] | Court House | CHWP/CTF | Court House CHWP/CTF | 1767
[23 empty] | Fire Station (Unmanned) | [14 empty] | Court House | HWP | Court House HWP | 6000
[23 empty] | Food Stores | [14 empty] | Dining: Bar Lounge/Leisure | FM | Dining: Bar Lounge/Leisure FM | 4182
[23 empty] | Gymnasium | [14 empty] | Dining: Bar Lounge/Leisure | CHWP/CTF | Dining: Bar Lounge/Leisure CHWP/CTF | 1923
[23 empty] | Hospitals | [14 empty] | Dining: Bar Lounge/Leisure | HWP | Dining: Bar Lounge/Leisure HWP | 6000
[23 empty] | Hospitals / Health Care | [14 empty] | Dining: Cafeteria / Fast Food | FM | Dining: Cafeteria / Fast Food FM | 6456
[23 empty] | Industrial - 1 Shift | [14 empty] | Dining: Cafeteria / Fast Food | CHWP/CTF | Dining: Cafeteria / Fast Food CHWP/CTF | 2742
[23 empty] | Industrial - 2 Shift | [14 empty] | Dining: Cafeteria / Fast Food | HWP | Dining: Cafeteria / Fast Food HWP | 6000
[23 empty] | Industrial - 3 Shift | [14 empty] | Dining: Family | FM | Dining: Family FM | 4182
[23 empty] | Laundromats | [14 empty] | Dining: Family | CHWP/CTF | Dining: Family CHWP/CTF | 1923
[23 empty] | Library | [14 empty] | Dining: Family | HWP | Dining: Family HWP | 6000
[23 empty] | Light Manufacturers | [14 empty] | Entertainment | FM | EntertainmentFM | 1952
[23 empty] | Lodging (Hotels/Motels) | [14 empty] | Entertainment | CHWP/CTF | EntertainmentCHWP/CTF | 1120
[23 empty] | Mall Concourse | [14 empty] | Entertainment | HWP | EntertainmentHWP | 6000
[23 empty] | Manufacturing Facility | [14 empty] | Exercise Center | FM | Exercise Center FM | 5836
[23 empty] | Medical Offices | [14 empty] | Exercise Center | CHWP/CTF | Exercise Center CHWP/CTF | 2518
[23 empty] | Motion Picture Theatre | [14 empty] | Exercise Center | HWP | Exercise Center HWP | 6000
[23 empty] | Multi-Family (Common Areas) | [14 empty] | Fast Food Restaurants | FM | Fast Food Restaurants FM | 6376
[23 empty] | Museum | [14 empty] | Fast Food Restaurants | CHWP/CTF | Fast Food Restaurants CHWP/CTF | 2713
[23 empty] | Nursing Homes | [14 empty] | Fast Food Restaurants | HWP | Fast Food Restaurants HWP | 6000
[23 empty] | Office (General Office Types) | [14 empty] | Fire Station (Unmanned) | FM | Fire Station (Unmanned) FM | 1953
[23 empty] | Office/Retail | [14 empty] | Fire Station (Unmanned) | CHWP/CTF | Fire Station (Unmanned) CHWP/CTF | 1121
[23 empty] | Parking Garages & Lots | [14 empty] | Fire Station (Unmanned) | HWP | Fire Station (Unmanned) HWP | 6000
[23 empty] | Penitentiary | [14 empty] | Food Stores | FM | Food Stores FM | 4055
[23 empty] | Performing Arts Theatre | [14 empty] | Food Stores | CHWP/CTF | Food Stores CHWP/CTF | 1877
[23 empty] | Police / Fire Stations (24 Hr) | [14 empty] | Food Stores | HWP | Food Stores HWP | 6000
[23 empty] | Post Office | [14 empty] | Gymnasium | FM | GymnasiumFM | 2586
[23 empty] | Pump Stations | [14 empty] | Gymnasium | CHWP/CTF | GymnasiumCHWP/CTF | 1348
[23 empty] | Refrigerated Warehouse | [14 empty] | Gymnasium | HWP | GymnasiumHWP | 6000
[23 empty] | Religious Building | [14 empty] | Hospitals | FM | HospitalsFM | 7674
[23 empty] | Residential (Except Nursing Homes) | [14 empty] | Hospitals | CHWP/CTF | HospitalsCHWP/CTF | 3180
[23 empty] | Restaurants | [14 empty] | Hospitals | HWP | HospitalsHWP | 6000
[23 empty] | Retail | [14 empty] | Hospitals / Health Care | FM | Hospitals / Health Care FM | 7666
[23 empty] | School / University | [14 empty] | Hospitals / Health Care | CHWP/CTF | Hospitals / Health Care CHWP/CTF | 3177
[23 empty] | Schools (Jr./Sr. High) | [14 empty] | Hospitals / Health Care | HWP | Hospitals / Health Care HWP | 6000
[23 empty] | Schools (Preschool/Elementary) | [14 empty] | Industrial - 1 Shift | FM | Industrial - 1 Shift FM | 2857
[23 empty] | Schools (Technical/Vocational) | [14 empty] | Industrial - 1 Shift | CHWP/CTF | Industrial - 1 Shift CHWP/CTF | 1446
[23 empty] | Small Services | [14 empty] | Industrial - 1 Shift | HWP | Industrial - 1 Shift HWP | 6000
[23 empty] | Sports Arena | [14 empty] | Industrial - 2 Shift | FM | Industrial - 2 Shift FM | 4730
[23 empty] | Town Hall | [14 empty] | Industrial - 2 Shift | CHWP/CTF | Industrial - 2 Shift CHWP/CTF | 2120
[23 empty] | Transportation | [14 empty] | Industrial - 2 Shift | HWP | Industrial - 2 Shift HWP | 6000
[23 empty] | Warehouse (Not Refrigerated) | [14 empty] | Industrial - 3 Shift | FM | Industrial - 3 Shift FM | 6631
[23 empty] | Waste Water Treatment Plant | [14 empty] | Industrial - 3 Shift | CHWP/CTF | Industrial - 3 Shift CHWP/CTF | 2805
[23 empty] | Workshop | [14 empty] | Industrial - 3 Shift | HWP | Industrial - 3 Shift HWP | 6000
[23 empty] | Other | [14 empty] | Laundromats | FM | Laundromats FM | 4056
[38 empty] | Laundromats | CHWP/CTF | Laundromats CHWP/CTF | 1878
[38 empty] | Laundromats | HWP | Laundromats HWP | 6000
[38 empty] | Library | FM | LibraryFM | 3748
[38 empty] | Library | CHWP/CTF | LibraryCHWP/CTF | 1767
[38 empty] | Library | HWP | LibraryHWP | 6000
[38 empty] | Light Manufacturers | FM | Light Manufacturers FM | 2857
[38 empty] | Light Manufacturers | CHWP/CTF | Light Manufacturers CHWP/CTF | 1446
[38 empty] | Light Manufacturers | HWP | Light Manufacturers HWP | 6000
[38 empty] | Lodging (Hotels/Motels) | FM | Lodging (Hotels/Motels) FM | 3064
[38 empty] | Lodging (Hotels/Motels) | CHWP/CTF | Lodging (Hotels/Motels) CHWP/CTF | 1521
[38 empty] | Lodging (Hotels/Motels) | HWP | Lodging (Hotels/Motels) HWP | 6000
[38 empty] | Mall Concourse | FM | Mall Concourse FM | 4833
[38 empty] | Mall Concourse | CHWP/CTF | Mall Concourse CHWP/CTF | 2157
[38 empty] | Mall Concourse | HWP | Mall Concourse HWP | 6000
[38 empty] | Manufacturing Facility | FM | Manufacturing Facility FM | 2857
[38 empty] | Manufacturing Facility | CHWP/CTF | Manufacturing Facility CHWP/CTF | 1446
[38 empty] | Manufacturing Facility | HWP | Manufacturing Facility HWP | 6000
[38 empty] | Medical Offices | FM | Medical Offices FM | 3748
[38 empty] | Medical Offices | CHWP/CTF | Medical Offices CHWP/CTF | 1767
[38 empty] | Medical Offices | HWP | Medical Offices HWP | 6000
[38 empty] | Motion Picture Theatre | FM | Motion Picture Theatre FM | 1954
[38 empty] | Motion Picture Theatre | CHWP/CTF | Motion Picture Theatre CHWP/CTF | 1121
[38 empty] | Motion Picture Theatre | HWP | Motion Picture Theatre HWP | 6000
[38 empty] | Multi-Family (Common Areas) | FM | Multi-Family (Common Areas) FM | 7665
[38 empty] | Multi-Family (Common Areas) | CHWP/CTF | Multi-Family (Common Areas) CHWP/CTF | 3177
[38 empty] | Multi-Family (Common Areas) | HWP | Multi-Family (Common Areas) HWP | 6000
[38 empty] | Museum | FM | MuseumFM | 3748
[38 empty] | Museum | CHWP/CTF | MuseumCHWP/CTF | 1767
[38 empty] | Museum | HWP | MuseumHWP | 6000
[38 empty] | Nursing Homes | FM | Nursing Homes FM | 5840
[38 empty] | Nursing Homes | CHWP/CTF | Nursing Homes CHWP/CTF | 2520
[38 empty] | Nursing Homes | HWP | Nursing Homes HWP | 6000
[38 empty] | Office (General Office Types) | FM | Office (General Office Types) FM | 3748
[38 empty] | Office (General Office Types) | CHWP/CTF | Office (General Office Types) CHWP/CTF | 1767
[38 empty] | Office (General Office Types) | HWP | Office (General Office Types) HWP | 6000
[38 empty] | Office/Retail | FM | Office/RetailFM | 3748
[38 empty] | Office/Retail | CHWP/CTF | Office/RetailCHWP/CTF | 1767
[38 empty] | Office/Retail | HWP | Office/RetailHWP | 6000
[38 empty] | Parking Garages & Lots | FM | Parking Garages & Lots FM | 4368
[38 empty] | Parking Garages & Lots | CHWP/CTF | Parking Garages & Lots CHWP/CTF | 1990
[38 empty] | Parking Garages & Lots | HWP | Parking Garages & Lots HWP | 6000
[38 empty] | Penitentiary | FM | PenitentiaryFM | 5477
[38 empty] | Penitentiary | CHWP/CTF | PenitentiaryCHWP/CTF | 2389
[38 empty] | Penitentiary | HWP | PenitentiaryHWP | 6000
[38 empty] | Performing Arts Theatre | FM | Performing Arts Theatre FM | 2586
[38 empty] | Performing Arts Theatre | CHWP/CTF | Performing Arts Theatre CHWP/CTF | 1348
[38 empty] | Performing Arts Theatre | HWP | Performing Arts Theatre HWP | 6000
[38 empty] | Police / Fire Stations (24 Hr) | FM | Police / Fire Stations (24 Hr) FM | 7665
[38 empty] | Police / Fire Stations (24 Hr) | CHWP/CTF | Police / Fire Stations (24 Hr) CHWP/CTF | 3177
[38 empty] | Police / Fire Stations (24 Hr) | HWP | Police / Fire Stations (24 Hr) HWP | 6000
[38 empty] | Post Office | FM | Post Office FM | 3748
[38 empty] | Post Office | CHWP/CTF | Post Office CHWP/CTF | 1767
[38 empty] | Post Office | HWP | Post Office HWP | 6000
[38 empty] | Pump Stations | FM | Pump Stations FM | 1949
[38 empty] | Pump Stations | CHWP/CTF | Pump Stations CHWP/CTF | 1119
[38 empty] | Pump Stations | HWP | Pump Stations HWP | 6000
[38 empty] | Refrigerated Warehouse | FM | Refrigerated Warehouse FM | 2602
[38 empty] | Refrigerated Warehouse | CHWP/CTF | Refrigerated Warehouse CHWP/CTF | 1354
[38 empty] | Refrigerated Warehouse | HWP | Refrigerated Warehouse HWP | 6000
[38 empty] | Religious Building | FM | Religious Building FM | 1955
[38 empty] | Religious Building | CHWP/CTF | Religious Building CHWP/CTF | 1121
[38 empty] | Religious Building | HWP | Religious Building HWP | 6000
[38 empty] | Residential (Except Nursing Homes) | FM | Residential (Except Nursing Homes) FM | 3066
[38 empty] | Residential (Except Nursing Homes) | CHWP/CTF | Residential (Except Nursing Homes) CHWP/CTF | 1521
[38 empty] | Residential (Except Nursing Homes) | HWP | Residential (Except Nursing Homes) HWP | 6000
[38 empty] | Restaurants | FM | Restaurants FM | 4182
[38 empty] | Restaurants | CHWP/CTF | Restaurants CHWP/CTF | 1923
[38 empty] | Restaurants | HWP | Restaurants HWP | 6000
[38 empty] | Retail | FM | RetailFM | 4057
[38 empty] | Retail | CHWP/CTF | RetailCHWP/CTF | 1878
[38 empty] | Retail | HWP | RetailHWP | 6000
[38 empty] | School / University | FM | School / University FM | 2187
[38 empty] | School / University | CHWP/CTF | School / University CHWP/CTF | 1205
[38 empty] | School / University | HWP | School / University HWP | 6000
[38 empty] | Schools (Jr./Sr. High) | FM | Schools (Jr./Sr. High) FM | 2187
[38 empty] | Schools (Jr./Sr. High) | CHWP/CTF | Schools (Jr./Sr. High) CHWP/CTF | 1205
[38 empty] | Schools (Jr./Sr. High) | HWP | Schools (Jr./Sr. High) HWP | 6000
[38 empty] | Schools (Preschool/Elementary) | FM | Schools (Preschool/Elementary) FM | 2187
[38 empty] | Schools (Preschool/Elementary) | CHWP/CTF | Schools (Preschool/Elementary) CHWP/CTF | 1205
[38 empty] | Schools (Preschool/Elementary) | HWP | Schools (Preschool/Elementary) HWP | 6000
[38 empty] | Schools (Technical/Vocational) | FM | Schools (Technical/Vocational) FM | 2187
[38 empty] | Schools (Technical/Vocational) | CHWP/CTF | Schools (Technical/Vocational) CHWP/CTF | 1205
[38 empty] | Schools (Technical/Vocational) | HWP | Schools (Technical/Vocational) HWP | 6000
[38 empty] | Small Services | FM | Small Services FM | 3750
[38 empty] | Small Services | CHWP/CTF | Small Services CHWP/CTF | 1768
[38 empty] | Small Services | HWP | Small Services HWP | 6000
[38 empty] | Sports Arena | FM | Sports Arena FM | 1954
[38 empty] | Sports Arena | CHWP/CTF | Sports Arena CHWP/CTF | 1121
[38 empty] | Sports Arena | HWP | Sports Arena HWP | 6000
[38 empty] | Town Hall | FM | Town Hall FM | 3748
[38 empty] | Town Hall | CHWP/CTF | Town Hall CHWP/CTF | 1767
[38 empty] | Town Hall | HWP | Town Hall HWP | 6000
[38 empty] | Transportation | FM | TransportationFM | 6456
[38 empty] | Transportation | CHWP/CTF | TransportationCHWP/CTF | 2742
[38 empty] | Transportation | HWP | TransportationHWP | 6000
[38 empty] | Warehouse (Not Refrigerated) | FM | Warehouse (Not Refrigerated) FM | 2602
[38 empty] | Warehouse (Not Refrigerated) | CHWP/CTF | Warehouse (Not Refrigerated) CHWP/CTF | 1354
[38 empty] | Warehouse (Not Refrigerated) | HWP | Warehouse (Not Refrigerated) HWP | 6000
[38 empty] | Waste Water Treatment Plant | FM | Waste Water Treatment Plant FM | 6631
[38 empty] | Waste Water Treatment Plant | CHWP/CTF | Waste Water Treatment Plant CHWP/CTF | 2805
[38 empty] | Waste Water Treatment Plant | HWP | Waste Water Treatment Plant HWP | 6000
[38 empty] | Workshop | FM | Workshop FM | 3750
[38 empty] | Workshop | CHWP/CTF | Workshop CHWP/CTF | 1768
[38 empty] | Workshop | HWP | Workshop HWP | 6000
[38 empty] | Other | FM | OtherFM | 3985
[38 empty] | Other | CHWP/CTF | OtherCHWP/CTF | 1852
[38 empty] | Other | HWP | OtherHWP | 6000
Note on C4: Facility Type Select the appropriate facility type from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours, Coincidence Factors, ESF and DSF (as applicable) for building types not listed.
Note on C5: Utility Select the utility serving the facility from the pull down menu.
Note on B10: Unique Motor I.D. Provide designation to identify the motor(s).
Note on D10: Number of Identical Units Number of motors that have the same motor function, load factor, configuration, manufacturer, model number, horsepower, speed, enclosure type, efficiency, and presence of VFD.
Note on E10: Load Factor Default Load Factor is 0.75. Customers wishing to adjust load factor must follow Custom Protocols for Motors and VFDs.
Note on F10: Motor Configuration Select the appropriate motor configuration. If the motor configuration is not listed, a custom motor protocol must be used. Single: One motor serving the load. Duplex: Two motors serving the load, one as standby.
Note on H10: Manufacturer Provide the motor manufacturer's name.
Note on I10: Model Number Provide the motor model number.
Note on J10: Motor Horsepower Select the rated horsepower of the motor.
Note on K10: Synchronous Speed Select one of the following: 1200 RPM = 6-pole 1800 RPM = 4-pole 3600 RPM = 2-pole
Note on L10: Enclosure Type Select the motor enclosure type: TEFC: Totally Enclosed Fan Cooled ODP: Open Drip Proof
Note on M10: Nominal Efficiency Input nominal efficiency from the motor nameplate. a) Input nameplate efficiency from exisiting motor if a VFD is installed on existing motor. b) Input nameplate efficiency from efficient motor if VFD is installed with motor replacement.
Note on N11: VFD on Motor Is there a VFD installed on this motor? Select "Yes" or "No". If existing motor already has a VFD installed, Custom Measure Protocols must be used.
Note on O11: VFD Baseline Select a VFD Baseline from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine ESF and DSF for VFD Baseline not listed. AFBI: Air Foil/Backward Incline AFBI IGV: Air Foil/Backward Incline with Inlet Guide Vanes FC: Forward Curved FC IGV: Forward Cureved with Inlet Guide Vanes CV: Constant Volume CHWP: Chilled Water Pump HWP: Heating Hot Water Pump
Note on P11: ESF "Energy Savings Factor" for the VFD. Percentage of energy consumption by motor when VFD is installed.
Note on Q11: DSF "Demand Savings Factor" for the VFD. Percentage of peak demand consumption by motor when VFD is installed.
Note on C10: Motor Function Select a motor function from the pull down menu. Custom Protocols for Motors and VFDs must be followed to determine Run Hours for motor functions not listed. FM: Fan Motor CHWP/CTF: Chilled Water Pump/ Cooling Tower Fan HWP: Heating Hot Water Pump
Note on K6: Program Year: Program Year 5: June 1, 2013 - May 31, 2014 Program Year 6: June 1, 2014 - May 31, 2015 Program Year 7: June 1, 2015 - May 31, 2016

## Summary
Savings Summary Form
Applicant Name: |  | Project Name:
Facility Name: |  | Survey completed by (name):
Facility Type: |  | Spot Measurements completed by (name):
Utility: |  | Date(s) Survey completed:
Installation Date: |  | Program Year:
Savings Data
Total Peak kW Reduction | 0
Total Annual kWh Savings | 0
|  |  | Utility | Facility Types
|  |  | Duquesne Light | Auto Related
|  |  | Met-Ed (FirstEnergy) | Bakery
|  |  | Penn Power (FirstEnergy) | Banks, Financial Centers
|  |  | PennElec (FirstEnergy) | Church
|  |  | West Penn Power (FirstEnergy) | College – Cafeteria
|  |  | PECO | College - Classes/Administrative
|  |  | PPL | College - Dormitory
Commercial Condos
Convenience Stores
Convention Center
Court House
Dining: Bar Lounge/Leisure
Dining: Cafeteria / Fast Food
Dining: Family
Entertainment
Exercise Center
Fast Food Restaurants
Fire Station (Unmanned)
Food Stores
Gymnasium
Hospitals
Hospitals / Health Care
Industrial - 1 Shift
Industrial - 2 Shift
Industrial - 3 Shift
Laundromats
Library
Light Manufacturers
Lodging (Hotels/Motels)
Mall Concourse
Manufacturing Facility
Medical Offices
Motion Picture Theatre
Multi-Family (Common Areas)
Museum
Nursing Homes
Office (General Office Types)
Office/Retail
Parking Garages & Lots
Penitentiary
Performing Arts Theatre
Police / Fire Stations (24 Hr)
Post Office
Pump Stations
Refrigerated Warehouse
Religious Building
Residential (Except Nursing Homes)
Restaurants
Retail
School / University
Schools (Jr./Sr. High)
Schools (Preschool/Elementary)
Schools (Technical/Vocational)
Small Services
Sports Arena
Town Hall
Transportation
Warehouse (Not Refrigerated)
Waste Water Treatment Plant
Workshop
Note on C4: Facility Type Select the appropriate facility type from the pull down menu.
Note on C5: Utility Select the utility serving the facility from the pull down menu.
Note on K6: Program Year: Program Year 1: June 1, 2009 - May 31, 2010 Program Year 2: June 1, 2010 - May 31, 2011 Program Year 3: June 1, 2011 - May 31, 2012 Program Year 4: June 1, 2012 - May 31, 2013

## Glossary
Pennsylvania Act 129 Motor and VFD Audit and Design Tool
GLOSSARY
Motor Form |  | VFD Form
Project Identification |  | Project Identification
Cell C2: | "Applicant Name" is the applicant name. | Cell C2: | "Applicant Name" is the applicant name.
Cell C3: | "Facility Name" is the facility name. | Cell C3: | "Facility Name" is the facility name.
Cell C4: | "Facility Type" is the facility classification. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient. | Cell C4: | "Facility Type" is the facility classification. The categories are based on the PA TRM. "Other" should be used when no other category is sufficient.
Cell C5: | "Utility" is the electric distribution company territory where the facility is located. | Cell C5: | "Utility" is the electric distribution company territory where the facility is located.
Cell C6: | "Date Submitted" is the date at which the application was submitted to the program. | Cell C6: | "Date Submitted" is the date at which the application was submitted to the program.
Cell K2: | "Project Name" is the name of the project. | Cell K2: | "Project Name" is the name of the project.
Cell K3: | "Survey Completed by (Name)" is the name of the inspector(s) who completed the survey. | Cell K3: | "Survey Completed by (Name)" is the name of the inspector(s) who completed the survey.
Cell K4: | "Spot Measurements Completed by (Name)" is the name of the inspector(s) who completed the spot measurements. | Cell K4: | "Spot Measurements Completed by (Name)" is the name of the inspector(s) who completed the spot measurements.
Cell K5: | "Date Survey(s) Completed" is the date at which the surveys were completed. | Cell K5: | "Date Survey(s) Completed" is the date at which the surveys were completed.
Cell K6: | "Program Year" is the program year in which the project was approved. | Cell K6: | "Program Year" is the program year in which the project was approved.
Motor Data |  | Motor Data
Column A: | "Line Item" indexes the motors. | Column A: | "Line Item" indexes the motors.
Column B: | "Unique Motor I.D.(s)" is an identifier for each motor. | Column B: | "Unique Motor I.D.(s)" is an identifier for each motor.
Column C: | "Motor Function" defines the function of the motor or the process served by the motor. There are three pre-defined motor functions: Fan Motor (FM), Chilled Water Pump (CHWP)/Cooling Tower Fan (CTF), and Heating Hot Water Pump (HWP). All other motor functions must be submitted as a custom measure. The combination of motor function, building type, and utility service territory determines the operating hours (column P). | Column C: | "Motor Function" defines the function of the motor or the process served by the motor. There are three pre-defined motor functions: Fan Motor (FM), Chilled Water Pump (CHWP)/Cooling Tower Fan (CTF), and Heating Hot Water Pump (HWP). All other motor functions must be submitted as a custom measure. The combination of motor function, building type, and utility service territory determines the ESF, DSF, and operating hours (columns P, Q and T).
Column D: | "Number of Identical Units" defines the quantity of motors for this particular line item. Motors that are not identical in Manufacturer, Model Number, Motor Function, Motor Configuration, Load Factor, Run Hours, Horsepower, Synchronous Speed, Enclosure Type, or Efficiency must be entered on separate lines. | Column D: | "Number of Identical Units" defines the quantity of motors for this particular line item. Motors that are not identical in Manufacturer, Model Number, Motor Function, Motor Configuration, Load Factor, Run Hours, Horsepower, Synchronous Speed, Enclosure Type, or Efficiency must be entered on separate lines.
Column E: | "Load Factor" is the ratio between the actual load and the rated load. Motor efficiency curves typically result in motors being most efficient at approximately 75% of the rated load. The default value is 0.75. | Column E: | "Load Factor" is the ratio between the actual load and the rated load. Motor efficiency curves typically result in motors being most efficient at approximately 75% of the rated load. The default value is 0.75.
Column F: | "Motor Configuration" is the setup in which the motor operates. For example, a motor may be in a single motor setup, parallel motor setup, a lead-lag setup, or a stand-by setup. Depending on the configuration, the coincidence factor will be changed. | Column F: | "Motor Configuration" is the setup in which the motor operates. For example, a motor may be in a single motor setup, parallel motor setup, a lead-lag setup, or a stand-by setup. Depending on the configuration, the coincidence factor will be changed.
Column G: | "Coincidence Factor" is the percentage of the motor load that is operating during electric system’s summer peak period as defined by Act 129. Heating hot water pumps do not operate during the summer cooling season and therefore the coincidence factor is 0. Chilled water pumps and condenser water pumps operate during the cooling season and therefore have a coincidence factor of 0.74. Pumps in a duplex or stand-by configuration have a 0.37 coincidence factor to account for the standby condition. Other motor configurations should follow custom protocols to determine the appropriate coincidence factor. | Column G: | "Coincidence Factor" is the percentage of the motor load that is operating during electric system’s summer peak period as defined by Act 129. Heating hot water pumps do not operate during the summer cooling season and therefore the coincidence factor is 0. Chilled water pumps and condenser water pumps operate during the cooling season and therefore have a coincidence factor of 0.74. Pumps in a duplex or stand-by configuration have a 0.37 coincidence factor to account for the standby condition. Other motor configurations should follow custom protocols to determine the appropriate coincidence factor.
Nameplate Data |  | Nameplate Data
Column H: | "Manufacturer" is the maker of the motor. | Column H: | "Manufacturer" is the maker of the motor.
Column I: | "Model Number" is the specific model number of the motor. | Column I: | "Model Number" is the specific model number of the motor.
Column J: | "Motor Horsepower" is the rated horsepower of the motor. | Column J: | "Motor Horsepower" is the rated horsepower of the motor.
Column K: | "Synchronous Speed" is the speed at which an induction motor will operate, which depends on the input power frequency and the number of electrical magnetic poles in the motor. Select either 1200 RPM, 1800 RPM, or 3600 RPM from the drop down menu. | Column K: | "Synchronous Speed" is the speed at which an induction motor will operate, which depends on the input power frequency and the number of electrical magnetic poles in the motor. Select either 1200 RPM, 1800 RPM, or 3600 RPM from the drop down menu.
Column L: | "Enclosure Type" is the enclosure of the fan which enables the cooling of motor windings. Select "ODP" for Open Drip Proof enclosure or "TEFC" for Totally Enclosed Fan Cooled from the drop down menu. | Column L: | "Enclosure Type" is the enclosure of the fan which enables the cooling of motor windings. Select "ODP" for Open Drip Proof enclosure or "TEFC" for Totally Enclosed Fan Cooled from the drop down menu.
Column M: | "Nominal Efficiency" is the ratio of the motor shaft output power to the electric input power. If the new motor is for new construction or to replace a failed motor, the baseline motor efficiency is the code standard. Complete Columns J, K, and L to populate the efficiency automatically. If the new motor is replacing a functioning motor, input the efficiency of the existing motor. For the new motor, directly input the nameplate efficiency. | Column M: | "Nominal Efficiency" is the ratio of the motor shaft output power to the electric input power. If the new motor is for new construction or to replace a failed motor, the baseline motor efficiency is the code standard. Complete Columns J, K, and L to populate the efficiency automatically. If the new motor is replacing a functioning motor, input the efficiency of the existing motor. For the new motor, directly input the nameplate efficiency.
Total per Unit |  | VFD
Column N: | "Full Load kW" is the maximum demand for the motor. This does not necessarily correspond to the peak demand, as coincidence factor has not been applied. | Column N: | "VFD on Motor" is to indicate the presence or absence of a VFD on the motor. If there is a VFD installed, select "Yes". If there is no VFD installed, select "No".
Column O: | "Peak kW" is the peak demand consumption for one motor in kilowatts. | Column O: | "Baseline" is the baseline for the VFD system, i.e. the control system previously in place before installing the new VFD system.
Column P: | "Operating Hours" is the number of hours that the motor runs in one year. This number is stipulated by building type and motor function.
|  | Column P: | "ESF" is the Energy Savings Factor for VFDs or the ratio of the motor energy usage with a VFD installed to the motor energy usage without a VFD installed. Motors with no VFD installed have an ESF of "1.00". This value can be looked up based on the baseline system.
Column Q: | "Annual kWh" is the total annual energy consumption of one motor in kilowatt-hours.
Total all Units
Column R: | "Peak kW" is the peak demand consumption of all the motors. | Column Q: | "DSF" is the Demand Savings Factor for VFDs or the ratio of the motor peak demand with a VFD installed to the motor peak demand without a VFD installed. Motors with no VFD installed have a DSF of "1.00". This value can be looked up based on the baseline system.
Column S: | "Annual kWh" is the total annual energy consumption of all the motors.
Total per Unit
|  | Column R: | "Full Load kW" is the maximum demand for the motor. This does not necessarily correspond to the peak demand, as coincidence factor has not been applied.
|  | Column S: | "Peak kW" is the peak demand consumption for one motor in kilowatts.
|  | Column T: | "Operating Hours" is the number of hours that the motor runs in one year. This number is stipulated by building type and motor function.
|  | Column U: | "Annual kWh" is the total annual energy consumption of one motor in kilowatt-hours.
Total all Units
|  | Column V: | "Peak kW" is the peak demand consumption of all the motors.
|  | Column W: | "Annual kWh" is the total annual energy consumption of all the motors.