| PENNSYLVANIA PUBLIC UTILITY COMMISSION Harrisburg, PA 17105-3265 |
| --- |
|  | Public Meeting held August 29, 2013 |
| Commissioners Present: Robert F. Powelson, Chairman John F. Coleman, Jr., Vice Chairman Wayne E. Gardner James H. Cawley Pamela A. Witmer |
| Pennsylvania Public Utility Commission, Bureau of Investigation and Enforcement v. UGI Penn Natural Gas, Inc. | M-2013-2338981 |

OPINION AND ORDER

BY THE COMMISSION:

Before the Pennsylvania Public Utility Commission (Commission) for consideration and disposition is a Settlement Agreement (Settlement) filed on August 16, 2013, by the Commission’s Bureau of Investigation and Enforcement (I&E) and UGI-Penn Natural Gas, Inc. (UGI-PNG).  Both Parties have filed a Statement in Support of the Settlement.

History of the Proceeding

On April 4 and 5, 2012, gas leaks were detected in a UGI-PNG main located along Pennsylvania Business Route 309 in Wilkes-Barre, Pennsylvania.  UGI-PNG initially performed a temporary repair and a permanent repair was completed on May 30, 2012.

As a result of this incident, the Commission’s Gas Safety Division (GSD) of I&E conducted an informal investigation of UGI-PNG’s leak classification, surveys, and compliance with state and federal regulations as well as UGI-PNG’s management’s compliance with pipeline repair practices.  Based on its investigation, I&E concluded that UGI-PNG was not compliant with state and federal regulations.

As a result of negotiations between UGI-PNG and I&E (hereinafter referred to collectively as Parties), the Parties agreed to resolve their differences in accordance with the Commission’s policy to promote settlements, 52 Pa. Code § 5.231.  On August 16, 2013, the Parties filed the Settlement Agreement.

Background

On April 4, 2012, a 911 dispatcher called UGI-PNG to report a natural gas odor in the vicinity of 460 Wilkes-Barre Township Boulevard, also known as Route 309.  UGI-PNG dispatched a first responder who performed a leak investigation at the site and graded the leak as an “A” leak.  Settlement at ¶ 10.  In grading the leak as “A,” the responder did not provide the other information that is requested on UGI-PNG’s leak form, such as the pressure of the main, the time of the leak investigation or other tracking information.  Id. at ¶ 11.

On May 12, 2012, an employee of a convenience store/gas station located at 464 Wilkes-Barre Township Boulevard called UGI-PNG to report a natural gas odor.  A UGI-PNG responder arrived at the location, performed an investigation, and determined it to be a “C” leak.  The leak record indicated the presence of elevated concentrations of gas in several bar holes along the road, and in a sanitary sewer manhole located in the road approximately twenty feet west of the convenience store/gas station parking lot.  Id. at ¶ 12.

The leaking pipeline at 464 Wilkes-Barre Township Boulevard was a ten-inch, unprotected, coated steel, high pressure distribution main operating at 320 Pounds per Square Inch (PSI) that was originally installed in 1961.  Id. at ¶ 13.

Later, on May 12, 2012, in an attempt to manage the leak, UGI-PNG installed three ten-inch diameter, Mueller full seal style 500 clamps side by side along the leaking pipe to allow for the welding of a Dresser 220 full encapsulation clamp.  This repair option was abandoned because the encapsulation clamp was insufficiently sized to allow for welding onto the pipe.  Leak monitoring bar test holes were drilled in the road and UGI-PNG determined that the Mueller clamps would be left in place until a permanent solution was implemented.  UGI-PNG backfilled the excavation and configured two valve boxes at the site to allow for the venting of any gas that might escape through the Mueller band clamps, which are pressure rated at 100 PSI, and not considered suitable for a permanent repair on a pipe operating at 320 PSI.  UGI-PNG did not reduce the pressure on this pipe prior to performing this temporary repair and the matter was referred to UGI-PNG Engineering to evaluate replacement options or to provide an alternative repair solution.  Id. at ¶ 14.

On May 13, 2012, a UGI-PNG supervisor visited the leak site and resurveyed the bar holes.  He determined that no hazardous conditions existed.  The supervisor’s actions in monitoring the leak were not documented.  Id. at ¶ 16.

From May 14, 2012, until 9:00 a.m. on May 16, 2012, no monitoring activity occurred at the leak site.  Id. at ¶¶ 17-18.

At 9:00 a.m. on May 16, 2012, UGI-PNG’s leak survey contractor rechecked the site and found elevated concentrations of gas in the bar holes.  Based on these findings, a UGI-PNG crew was dispatched to the site.  The crew drilled additional bar holes and discovered gas migrating underneath the concrete island at the convenience store/gas station parking lot apron and into the grass curb line.  The contractor submitted a “C” leak report.  Id. at ¶ 20.

From 10:00 a.m. until 1:00 p.m. on May 16, 2012, the utility reduced pressure in the line from approximately 300 PSI to 200 PSI.  UGI-PNG re-excavated the original dig site and tightened one of the three clamps.  After purging gas from the soil, lesser concentrations of gas were detected by UGI-PNG’s crew.  A few hours later, the site was rechecked by the UGI-PNG leak survey contractor and based on the excavation and tightening of the leak clamp above, the contractor submitted a “B” leak report.  The utility continued purging residual gas throughout this period.  Id. at ¶ 21.

Between May 17 and 20, 2012, UGI-PNG monitored the leak site.  Whenever the levels became elevated, the UGI-PNG crews purged the soil until the readings were lowered to zero.  UGI-PNG personnel remained on site continuously from this point forward until the main section of the line with the leak clamps was taken out of service.  Id. at ¶ 22.

On May 20, 2012, the GSD received an email from a Pipeline and Hazardous Materials Safety Administration (PHMSA) representative regarding National Response Center (NRC) report #1011999, dated May 19, 2012.  The NRC report stated that a person describing himself as a UGI-PNG employee alleged that a leak on a high pressure gas distribution line was discovered and subsequently repaired by the Company using improper clamps on Saturday, May 12, 2012, that “the clamps used for the repair blew out on Tuesday, May 15,” and that “the gas company may be trying to cover up the release.”  The GSD began an investigation.  Id. at ¶ 23.

During the period from May 22-25, 2012, UGI-PNG’s contractor repaired the line.  UGI-PNG monitored the site and continued to purge the leak site until the repair was completed.  On May 30, 2012, UGI-PNG completed the repair and reactivated the line.  Leak checks at that time showed zero levels of gas.  Id. at ¶ 26.

At the GSD’s request, the retired pipe section was removed on May 29, 2012.  Examination of the pipe revealed corrosion pits on approximately five feet of the pipe.  The depth and pattern of the pits were indicative of corrosion caused by electrical interference.  Thereafter, field testing concluded that a source of the interference current on the high pressure main was the rectifier used for cathodically protecting equipment at a nearby gasoline filling station located east of the leak site.  Id. at ¶ 27.

The pipe in question is part of a two-mile unprotected steel line that, prior to April 4, 2012, experienced twelve leaks since 1986.  Three of those leaks occurred during the six-year period after UGI-PNG acquired the gas system in October 2006.  Id. at ¶ 28.

UGI-PNG determined that the segment of pipeline at issue was leak surveyed routinely through mobile and walking surveys.  Id. at ¶ 29.

As a result of the Route 309 incident, the GSD conducted an expanded investigation of UGI-PNG’s leak classification, surveys and management systems, and compliance with state and federal regulations.  Id. at ¶ 30.  I&E concluded that UGI-PNG was not compliant with state and federal regulations in that UGI-PNG: (1) inadequately monitored and repaired leaks; (2) incorrectly classified leaks; (3) inadequately documented and maintained documentation of leak survey and dispatch data; and (4) improperly used and documented its use of the Emergency One Call System.  Id. at ¶ 32.  As noted, I&E and UGI-PNG engaged in negotiations and a Settlement Agreement subsequently was executed and filed with the Commission on August 16, 2013.

If these matters had been litigated, I&E would have contended that UGI-PNG committed the following acts or omissions in relation to the Route 309 incident:

      - UGI-PNG violated its operating procedure GOM 60.50.30 in that on April 4, 2012, UGI-PNG failed to ascertain sufficient information to properly grade the leak, including uncovering the potential hazard, proceeding to the street and checking manholes.  There is no indication on the leak form that this action was performed.

      - UGI-PNG exceeded the main’s MAOP in that on May 12, 2012, UGI-PNG installed clamps rated for 100PSI on the main which was operating at 320PSI.  There was no pressure reduction prior to attempting this repair.

      - UGI-PNG failed to properly repair the main on May 12, 2012 in that it back-filled the soil and departed from the scene after installing incorrectly rated band clamps and vents.

      - UGI-PNG failed to adequately monitor a hazardous condition after backfilling the excavation on May 12, 2012 in that it departed the scene after leaving improperly rated clamps on a hazardous leak. Exceeding MAOP constitutes an emergency condition that warrants monitoring.  UGI-PNG failed to perform reasonable safety measures such as continuously monitoring by leaving a technician on-scene.

      - UGI-PNG violated its procedures in that it failed to document the supervisor’s actions when he checked readings from the leak on May 13, 2012.  UGI-PNG’s procedures state that “All leak survey information shall be recorded, tabulated, and maintained in accordance with Company policy to enable the completion of the Department of Transportation Leak Report (DOT F-7100.1-1 and various other reports for inter-company use.”  See UGI-PNG Procedures and Methods 5-1 section B, regarding “Documentation.”

      - UGI-PNG failed to cathodically protect the high pressure distribution line at 460 Wilkes Barre Boulevard.  This line required cathodic protection in that it was part of a pre-1971, unprotected steel segment that experienced significant leak history due to corrosion.  After September 15, 2003, thirteen (13) leaks were found on this section of the main, which indicate active corrosion as defined by 49 CFR § 192.3.  Bare or coated distribution lines installed prior to August 1, 1971, must be cathodically protected when active corrosion exists.

      - UGI-PNG failed to reevaluate and document the reevaluation of unprotected pipelines every three years, which must be monitored to detect areas of active corrosion.

      - The leak was determined to be caused by interference current from a gas station rectifier.  UGI-PNG failed to employ a program to minimize the effects of interference.

      - UGI-PNG failed to cathodically protect 24 of the service lines in the unprotected segment.  These lines were installed after July 1971.

      - UGI-PNG returned to service a new segment of pipeline or a segment of pipeline that was relocated or replaced before substantiating the MAOP of that pipeline in that UGI-PNG has records revealing 24 pressure tests at 100PSI or below.  The main operated at 320PSI and the service lines would need to be pressure tested to at least 480PSI to meet the pressure testing requirements for the MAOP of the main.

      - UGI-PNG failed to document the condition of the main, which was exposed after installation of each of the 24 service lines.  UGI-PNG cannot produce inspection records that indicate that the main was examined for evidence of external corrosion.

      - UGI-PNG could not produce any documentation to substantiate the established MAOP of the main.

Settlement at 9-10.  I&E noted that, if proven, the alleged UGI-PNG acts and omissions, above, would constitute violations of Section 1501 of the Public Utility Code (Code), 66 Pa. C.S. § 1501, and the following state and federal regulations:  52 Pa. Code § 59.33(a); 49 C.F.R. §§ 192.13, 192.455, 192.457, 192.459, 192.465, 192.473, 192.503, 192.603, 192.605, 192.615, 192.619, 192.702.

Had this matter been fully litigated, UGI-PNG would have denied or answered and defended against many, if not all, of the above stated allegations.  Settlement at ¶ 35.

Terms of the Settlement Agreement

The Parties state that the purpose of the Settlement is to terminate the investigations in this proceeding and to resolve these matters without litigation.  Settlement at ¶ 36.  The Settlement provides that it resolves with prejudice all issues related to the informal investigation.  Id. at ¶ 41.  The Settlement notes that throughout the entire investigatory process, UGI-PNG had been cooperative and proactive with I&E’s recommendations and has already undertaken steps to complete some of the remedies set forth in the Settlement.  Id. at ¶ 37.

The Parties have agreed that, pursuant to the Settlement terms set forth below, UGI-PNG will perform the following:

  - Pay a civil penalty in the amount of one million dollars ($1,000,000.00), pursuant to 66 Pa. C.S. § 3301(c).  Payment shall be made by certified check made payable to the “Commonwealth of Pennsylvania” and forwarded to the Commission through the prosecuting attorney within thirty (30) days of the date of entry of the Commission’s Order.  UGI-PNG shall not include any portion of this civil penalty in any future rate proceeding, nor shall it be tax deductible under Section 162(f) of the Internal Revenue Code, 26 U.S.C.S. § 162(f).

  - Within ninety (90) days after the date on which a final order approving this Settlement without modification is entered, or by March 31, 2014, whichever date occurs later, UGI-PNG shall implement an automated, computer-based system of recording and tracking the results of leak surveys that will be utilized both by UGI-PNG’s employees and outside contractors performing leak surveys, mapping, investigations and repairs.  Until such automated system is implemented, outside contractors shall be required by UGI-PNG to maintain records of leak surveys conducted by the contractor for UGI-PNG for a period of no less than two (2) years.

  - Within ninety (90) days after the date on which a final order approving this Settlement without modification is entered, UGI-PNG shall provide to I&E the results of the 3rd party audit UGI commissioned to evaluate “B” leak classification and repair.  The audit encompassed all active recorded PNG “B” leaks as of December 31, 2012 and “C” leaks repaired from October 1 through December 31, 2012.  The written report shall address the accuracy of characterization of all “B” leaks, and the quality of repair for all “C” leaks included in the audit.  Within one hundred twenty (120) days after the date on which a final order approving this Settlement without modification is entered, UGI-PNG shall provide to I&E the results of the audit or recheck that encompassed all active recorded “A” leaks in Wilkes-Barre Township and Borough, and Scranton discovered in 2012.

  - By no later than the end of the ninth (9th) full calendar month after the date on which a final order of the Commission approving this Settlement without modification is entered, UGI-PNG shall provide I&E with a completed audit report of UGI-PNG’s gas operations by an outside consultant hired by UGI-PNG.  The report shall include the auditor’s findings and recommendations, UGI-PNG’s position on the auditor’s findings and recommendations, and UGI-PNG’s implementation plan.  The operational audit shall review all material practices and procedures related to the items identified in the attached document entitled “Scope and Controls for the UGI-PNG Management Audit M-2013-2338981” attached hereto as Appendix C.

  - Commencing within ninety (90) days after the date on which a final order approving this Settlement without modification is entered, UGI-PNG shall implement a modified leak survey program of its entire inventory of unprotected steel distribution mains and cast iron pipe, which will require two additional leak survey cycles per year, during non-winter months.

For a period of two years, the survey results will be submitted to I&E on a quarterly basis within thirty (30) days of completion and will include leak reports/classification sheets.  After this two year period, UGI-PNG will assess the value of continuing this program in connection with the annual Distribution Integrity Management Plan review following the end of the two-year period.

  - Within twelve (12) months following the date on which a final order approving this Settlement without modification is entered, UGI-PNG shall submit to the GSD the following information regarding any high pressure distribution pipeline currently operating at 100PSI or greater within the UGI-PNG service territory:

1. 	Identify by location and length for each pipeline, the physical characteristics broken down into individual segments defined by pipe material, joining procedure, diameter, wall thickness, grade, protected, unprotected, coasting and year installed.

2. 	Provide the actual operating pressures listed annually, both low and high, for each segment since calendar year 2000 and the corresponding calculated SMYS for each segment according to 49 CFR § 192.107(b).

3. 	Provide the MAOP of each high pressure distribution pipeline.  Provide all supporting documents.

4. 	Provide the leak history for each pipeline in tabular form and include the documentation in the form of pipe inspection reports.

5. 	A plan to establish operating parameters for any distribution main segments for which UGI-PNG cannot adequately confirm the MAOP.  Factors to be considered in developing the plan shall include, at a minimum, operating history, location, potential consequences, and estimated cost of confirming MAOP, and any federal initiatives related to the topic.  The Commission shall determine the appropriate process for reviewing the reasonableness of UGI-PNG’s proposed plan.

  - Provide a list of all UGI-PNG unprotected pipeline, including its location, to the GSD within thirty (30) days of the approval of this Settlement Agreement.

  - For a period of one year after the date on which a final order of the Commission approving this Settlement without modification is entered, UGI-PNG shall not be subject to further sanction or non-compliance finding that could be imposed by the Commission or the GSD regarding any or all subject matter covered by this Settlement, except in matters involving an “incident,” as defined in 49 C.F.R. § 191.3, or a “safety related condition report,” as defined by 49 C.F.R. § 191.23(a).

Settlement at ¶ 37.

In consideration of UGI-PNG’s agreement to pay a $1,000,000.00 civil penalty and implementation of other measures, as specified herein, I&E agrees to forebear from prosecuting any formal complaint that relates to UGI-PNG’s conduct as described in the Settlement.  The Parties state that nothing contained in this Settlement shall adversely affect the Commission’s authority to receive and resolve any informal or formal complaints filed by any affected party with respect to the incident, except that no further civil penalties may be imposed by the Commission for any actions identified in the Settlement.  Id. at ¶ 38.  Additionally, none of the provisions of the Settlement or the statements in the Settlement shall be considered an admission of any fact or culpability.  Id. at ¶ 40.  As the Settlement does not make any findings of fact or conclusions of law, the Parties intend that the Settlement shall not be admitted as evidence in any potential civil proceeding involving this matter.  Id. at ¶ 41.

The Settlement is conditioned upon the Commission’s approval of its terms, without modification.  Id. at ¶ 43.  The Parties reserve the right to withdraw from the Settlement Agreement if it is modified.  Id. at ¶ 44.

We note that, consistent with Section 5.231 of our Regulations, 52 Pa. Code § 5.231, it is our policy to promote settlements.  However, before taking final action on the proposed Settlement Agreement, we must first seek public comment pursuant to Section 3.113(b)(3) of our Regulations, 52 Pa. Code § 3.113(b)(3).

Conclusion

Before issuing a decision on the merits of the proposed Settlement, consistent with Section 3.113(b)(3) of our Regulations, 52 Pa. Code § 3.113(b)(3), we are providing an opportunity for interested parties to file comments; THEREFORE,

IT IS ORDERED:

1.	That this Opinion and Order, together with the attached Settlement Agreement and the Statements in Support thereof, shall hereby be entered for comments.

2.	That a copy of this Opinion and Order together with the attached Settlement Agreement and the Statements in Support thereof, shall be served on the Office of Consumer Advocate, the Office of Small Business Advocate and the Bureau of Investigation and Enforcement.

3.	That comments to this Opinion and Order, together with the Settlement Agreement and the Statements in Support thereof, will be considered timely if filed within twenty (20) days of the date of entry of this Opinion and Order.

4.	That, subsequent to the Commission’s review of the comments filed in this proceeding, a final Opinion and Order will be issued.

BY THE COMMISSION,

Rosemary Chiavetta

Secretary

(SEAL)

ORDER ADOPTED: August 29, 2013

ORDER ENTERED:  August 29, 2013

ATTACHMENT

# Footnotes

UGI-PNG procedures define an “A” leak as a leak that is non-hazardous at the time of detection and can be reasonably expected to remain non-hazardous.

UGI-PNG procedures define a “C” leak as a leak that is an existing or possible hazard to persons or property that requires immediate repair or continuous action until the conditions are no longer hazardous.

UGI-PNG procedures define a “B” leak as a non-hazardous leak at the time of detection, but justifies scheduled repair based on probable future hazard.