	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held October 22, 2015

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	John F. Coleman, Jr., Vice Chairman
	

	Pamela A. Witmer
	

	Robert F. Powelson
Andrew G. Place
	

	
	


	Letter of Notification of PECO Energy Company, filed pursuant to 52 Pa. Code §57.72 57 Subchapter G for the Construction of 230 kV Transmission Facilities to Connect the Post Substation to the Transmission Grid in the Borough of Marcus Hook and Lower Chichester Township, Delaware County, Pennsylvania 
	Docket Number:

A-2015-2496384


ORDER

BY THE COMMISSION:

On July 31, 2015, PECO Energy Company (PECO), Utility Code 110550, filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(l)(vi) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated “Letter of Notification” (LON) siting application process in lieu of an application for the following:

(i)
An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 
right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code §57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Marcus Hook Borough, Lower Chichester Township, Delaware County Planning Commission and Delaware County Commissioners.  No protests were filed.  No hearings were held.

PECO requests approval to construct approximately 0.35 mile of new transmission facilities to electrically connect the new Post Substation to the existing transmission grid.  The Post Substation will serve the growing electric distribution load in the immediate area, including load at Sunoco Partners’ Marcus Hook refinery.  

The Post Substation will be located on land that is currently part of the Sunoco Partner’s Marcus Hook refinery, and for which PECO has an easement for this use.  PJM has designated this project including the Post Substation as a supplemental project with project number id s1002.  The project was presented at the July 29, 2015, Mid-Atlantic TEAC meeting as a solution to improve reliability due to load growth.


The proposed line will be comprised of seven towers – one inside the substation fence, two to traverse a portion of the industrial refinery to reach the existing transmission grid and four on the existing transmission right-of-way to complete the interconnection to the grid.  The new structures range from 80 to 130 ft. high.  The new line section is proposed to tie in two circuits (line-in and line-out) approximately 0.35 miles long into the new substation to the existing 220-39 line.  The proposed line section will tie into PECO’s 220-39 line between structures 287 and 287A.  Structure 287 is 90 feet tall and Structure 287A is 97 feet tall.  
PECO maintains that design, construction and operation of the proposed project will meet or exceed the requirements specified by the National Electric Safety Code (NESC).  PECO states that for new construction such as this project, PECO designs the facilities to meet the NESC guidelines, plus a minimum of an additional 3 feet of additional vertical clearance.  

A right-of-way (ROW) width of a minimum of 150 ft. is provided for the proposed new overhead line segment where both circuits are supported on dual circuit structures.  At the tie-in location, the circuits split and are supported on individual structures.  The ROW expands to 224 feet at the 220-39 line tie-in and 223 feet at the substation tie-in.  PECO provides that this exceeds the requirements of the NESC and PECO’s Engineering Practice EPP-2090 “OHT Design Clearances” and will provide access for line maintenance, repair and vegetation management.

PECO states that the total estimated cost for the proposed project is approximately $8.0 Million, and will be owned and paid for by PECO.  Construction of the line is proposed to commence in October 2015 with a proposed in-service date of August 31, 2016.    
The formal PECO Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the proposed addition of the new transmission line is less than 2.0 miles.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not reach the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by the PECO Electric Company for the Construction of 230 kV Transmission Facilities to Connect the Post Substation to the Transmission Grid in the Borough of Marcus Hook and Lower Chichester Township, Delaware County, Pennsylvania, is hereby approved.  
2. That this proceeding at Docket No. A-2015-2496384 be closed. 
BY THE COMMISSION,

[image: image1.png]



Rosemary Chiavetta
Secretary

ORDER ADOPTED: October 22, 2015
ORDER ENTERED:  October 22, 2015
5

