	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held October 22, 2015

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	John F. Coleman, Jr., Vice Chairman
	

	Pamela A. Witmer
	

	Robert F. Powelson
Andrew G. Place
	

	
	


	Letter of Notification of PECO Energy Company, filed pursuant to 52 Pa. Code §57.72 57 Subchapter G for the Reconfiguration of a Segment of PECO’s 220-24 230 kV Transmission Line in Peach Bottom Township, York County, Pennsylvania 
	Docket Number:

A-2015-2496406


ORDER

BY THE COMMISSION:

On July 31, 2015, PECO Energy Company (PECO), Utility Code 110550, filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(l)(vi) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated “Letter of Notification” (LON) siting application process in lieu of an application for the following:

(i)
An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 
right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code §57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Peach Bottom Township, York County Planning Commission and York County.  No protests were filed.  No hearings were held.

PECO requests approval to construct approximately 0.33 mile of new transmission facilities immediately adjacent to an existing substation and terminal yard to replace the existing electrical connection between those facilities.  This transmission work will replace the existing underground transmission facility that connects PECO’s Peach Bottom North Substation and PECO’s Peach Bottom Terminal Yard.  PECO states that the underground line is a 230 kV Low-Pressure Fluid-Filled (LPFF) underground cable nearing the end of its useful life.  The LPFF cable technology in use at this site is no longer being manufactured.  PECO is therefore replacing the existing underground LPFF cable with an aerial 230 kV transmission line.  The new line will be comprised of four new transmission towers (one tubular and three H-frames).  The new structures range from 80 to 123 feet high.  The new 230 kV line will cross over the right-of-way of an existing 500 kV line.  The 500 kV line structures are 110 - 120 ft. high.  
PECO maintains that design, construction and operation of the proposed project will meet or exceed the requirements specified by the National Electric Safety Code (NESC).  PECO states that for new construction such as this project, PECO designs the facilities to the NESC guidelines, plus a minimum of an additional 3 feet of vertical clearance and an additional 2 feet of horizontal clearance.   

The right-of-way (ROW) for this project will be a minimum of 150 feet in width.  PECO and Exelon Generation Company, LLC have an agreement where PECO has an easement to construct, operate and maintain substation and transmission facilities on Peach Bottom Atomic Power Station land.  Exelon has granted approval for the easement for the new 150 foot ROW corridor.    

PECO states that the total estimated cost for the proposed project is approximately $4.4 million, and will be owned and paid for by PECO.  Construction of the line is proposed to commence in September 2015 with a proposed in-service date of June 30, 2016.    
The formal PECO Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the proposed addition of the new transmission line is less than 2.0 miles.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not reach the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by the PECO Electric Company for the Reconfiguration of a Segment of PECO’s 220-24 230 kV Transmission Line in Peach Bottom Township. York County, Pennsylvania, is hereby approved.  
2. That this proceeding at Docket No. A-2015-2496406 be closed. 
BY THE COMMISSION,

[image: image1.png]



Rosemary Chiavetta
Secretary

ORDER ADOPTED: October 22, 2015
ORDER ENTERED:  October 22, 2015
4

