	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held April 7, 2016

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
	

	Pamela A. Witmer
	

	John F. Coleman, Jr.
	

	Robert F. Powelson
	


	Letter of Notification of PPL Electric Utilities Corporation, filed pursuant to 52 Pa. Code §57.72 57 Subchapter G for Approval to Rebuild Approximately 24.4 Miles of the Existing Susquehanna-Jenkins 230 kV Transmission Line Located in Luzerne County, Pennsylvania 
	Docket Number:

A-2016-2526304


ORDER

BY THE COMMISSION:

On January 29, 2016, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification pursuant to 52 Pa. Code §57.72(d)(v) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated “Letter of Notification” (LON) siting application process in lieu of an application for the following:

(i)
An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 
right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.

Copies of the Letter of Notification were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code §57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Luzerne County Commissioners, Luzerne County Planning Commission,  Conyngham Township, Slocum Township, and others.  No protests were filed.  No hearings were held.

PPL Electric requests approval to reconstruct approximately 24.4 miles of the existing single-circuit Susquehanna-Jenkins 230 kV transmission line as a double-circuit 230 kV line in Conyngham Township, Slocum Township, Nuangola Borough, Rice Township, Hanover Township, Bear Creek Township, Laurel Run Borough, and Plains Township, Luzerne County, Pennsylvania.  According to PPL Electric, the new segments and rebuilt 230 kV transmission line is needed to resolve a thermal violation identified by PJM Interconnection, LLC (PJM) in the 2013 Regional Transmission Expansion (RTEP) analysis.   
PPL Electric provides that the proposed project consists of rebuilding approximately 24.4 miles of the existing 26.5 mile single-circuit Susquehanna-Jenkins 230 kV Transmission Line between the Susquehanna 230-69 kV Substation in Conyngham Township to a new tap point near the Jenkins 230-69 kV Substation in Plains Township to a double-circuit configuration.  The new double-circuit system will tap into the existing Jenkins-Acahela 230 kV Transmission Line located approximately 2.1 miles south of the Jenkins 230-69 kV Substation. 
PPL Electric explains that at the tap point, one of the two circuits will tap into and continue north on the existing Jenkins-Acahela 230 kV Transmission Line and will terminate at the Jenkins 230-69 kV Substation.  This circuit will continue to be referred to as the Susquehanna-Jenkins 230 kV Transmission Line.  The other circuit will tap into and continue south on the existing Jenkins-Acahela 230 kV Transmission Line and will terminate at the Acahela 230-69 kV Substation.  This circuit will be referred to as the Susquehanna – Acahela 230 kV Transmission Line.   
PPL Electric indicates that the rebuilt transmission line will be located within the existing right-of-way for the Susquehanna-Jenkins 230 kV Transmission Line, which is 150-feet wide for the majority of the line with several locations increasing to 250-feet or more.  The rebuilt double-circuit line will be constructed on the existing centerline with each new structure located adjacent to the existing structures.  PPL Electric maintains that no new additional right-of-way is necessary for the proposed project.   

PPL Electric notes that the first four tower structures from the Susquehanna 230-69 kV Substation currently are double-circuit structures, with one side occupied by the existing single-circuit Susquehanna-Jenkins 230 kV Transmission Line and the other side occupied by the existing Susquehanna-Mountain 230 kV Transmission Line.  In order to rebuild the Susquehanna-Jenkins 230 kV Transmission Line for double-circuit operation, the Susquehanna-Mountain 230 kV Transmission Line will be removed from Structures 1 through 4 from the Susquehanna 230-69 kV Substation and relocated onto five new steel monopoles located entirely on PPL Electric-owned property within the substation property.  The changes to the existing Susquehanna-Mountain 230 kV Transmission Line are part of this LON application.
PPL Electric states that the existing single-circuit Susquehanna-Jenkins 230 kV Transmission Line consists of nine steel poles and 132 lattice tower structures, with an average height of 100 feet.  The existing towers will be replaced by self-weathering tubular steel structures with an average height of 150 feet.  All new poles will be self-supported on concrete caisson foundations.  The average spans between the structures will be approximately 1,100 feet.  The new poles are within 125 feet of the existing towers and poles with the exception of one pole within 250 feet of the existing tower and another within 500 feet.  No new poles will be placed on any property that currently does not have an existing tower or pole.  
PPL maintains the Project will be designed to comply with, and generally exceed, current National Electrical Safety Code (NESC) standards.  Design specifications and safety rules practiced by PPL Electric are set forth in PPL Electric’s Design Criteria and Safety Practices.  PPL Electric provides that its transmission lines are designed to operate safely and reliably during inclement weather even more severe than assumed by the NESC.  In addition, PPL Electric transmission lines are designed with more clearance to the ground than required by the NESC.  
PPL Electric states that the total estimated cost for the proposed project is approximately $64.3 million, and will be owned and operated by PPL Electric.  The proposed project was included in the 2013 RTEP as baseline project b2269.  Construction of the project is proposed to commence in September 2016 with a proposed in-service date of June 2018.    
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(v) because the reconstructed 22.4 mile 230 kV transmission line will be located entirely within PPL Electric’s existing rights-of-way.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not reach the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric Utilities Corporation, for Approval to Approval to Rebuild Approximately 24.4 Miles of the Existing Susquehanna-Jenkins 230 kV Transmission Line Located in Luzerne County, Pennsylvania, is hereby approved.  
2. That the proposed changes to the Susquehanna-Mountain 230 kV Transmission Line which will be removed from Structures 1 through 4 from the Susquehanna 230-69 kV Substation and relocated onto five new steel monopoles located entirely on PPL Electric-owned property within the substation property, is hereby approved.  
3. That this proceeding at Docket No. A-2016-2526304 be closed. 
[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

ORDER ADOPTED: April 7, 2016
ORDER ENTERED:  April 7, 2016
6

