BEFORE THE

PENNSYLVANIA PUBLIC UTILITY COMMISSION

John J. Rounce						:

:

v.						:		C-2015-2506941

:

:

PECO Energy Company				:

# INITIAL DECISION

Before

Eranda Vero

Administrative Law Judge

This Initial Decision dismisses John J. Rounce’s Complaint against PECO Energy Company upon finding that Complainant has failed to carry his burden of proof with respect to his reliability and safety claims against the Respondent.

history of the proceeding

On September 30, 2015, John J. Rounce (Mr. Rounce or Complainant) filed a formal Complaint (Complaint) against PECO Energy Company (PECO, Respondent, or the Company) alleging that he was having a reliability, safety or quality problem with his electricity service.  In particular, Mr. Rounce avers that in his 30 years as a PECO customer he has experienced problems with numerous outages, surges, spikes and brownouts which have persisted despite his complaints to PECO.  As relief, Mr. Rounce requests that the Commission conduct independent testing and investigate the surges, spikes, and brownouts that occur on the PECO line which services his residence.

On October 26, 2015, PECO filed an Answer denying the material allegations of the Complaint.

A Hearing Notice dated November 12, 2015, notified the parties that an initial hearing was scheduled for Monday, February 1, 2015, at 10:00 a.m.

A Prehearing Order was issued on December 4, 2015, advising the parties of the date and time of the scheduled hearing, informing them of the procedures applicable to this proceeding, and directing the submission of documents prior to the hearing.

The hearing convened as scheduled on February 1, 2016.  Mr. Rounce appeared pro se and testified on behalf of the Complaint.  He sponsored seven exhibits, six of which (Complainant Exhibits 1-3, and 5-7) were admitted into the record in this matter.  Shawane L. Lee, Esq. represented the Respondent, and presented the testimony of Nathaniel Nichols – who is a PECO engineer for regional engineering design; and Jeffrey Watson – who is a senior project manager with PECO in its Vegetation Management Department.  The Respondent sponsored eight exhibits all of which were admitted into the record in this matter.

The record in this matter closed on March 2, 2016.

FINDINGS OF FACT

- The Complainant is John J. Rounce, who resides at 9 Forest Lake Drive, Media, PA 19063 (Service Address).

- The Respondent is PECO Energy Company.

3.	Mr. Rounce’s service line is fed by a 34 kV circuit known as Middletown 352, which runs along PA Route 352.  Tr. 41.

4.	The Middletown 352 circuit crosses hilly terrain and heavily wooded areas characterized by tall, mature trees with large canopies.  Tr. 143.

5.	While the power lines within Mr. Rounce’s development are underground, the main portion of the Middletown 352 circuit consists of aerial lines.  Tr. 56.

Outages, Spikes and Surges

6.	A sustained outage is any outage that lasts over five minutes.  Tr. 65, 120.

7.	A momentary outage is any outage that lasts less than five minutes.  Tr. 65.

8.	From January 1, 2011 to January 1, 2016, PECO recorded 18 sustained outages affecting Mr. Rounce’s service.  Tr. 69, PECO Exhibit 1.

9.	On February 2, 2011, a tree growth came into contact with PECO’s primary wires causing an outage that lasted for six hours and eight minutes and affected 1,301 PECO customers, including Mr. Rounce.  Tr. 86, PECO Exhibit 1.

10.	On April 30, 2012, a contractor hired by a neighbor of Mr. Rounce hit PECO’s underground secondary wire causing an outage which lasted for two hours and 33 minutes and affected seven PECO customers, including, Mr. Rounce.  Tr. 85-86, PECO Exhibit 1.

11.	On October 29, 2012, a broken tree limb or trunk fell on PECO’s equipment causing an outage which lasted one hour and 13 minutes and affected 294 customers, including Mr. Rounce.  Tr. 85, PECO Exhibit 1.

12.	On October 7, 2013, a tree limb came into contact with primary wires causing an outage which lasted 53 minutes and affected 294 customers, including Mr. Rounce.  Tr. 85, PECO Exhibit 1.

13.	On February 5, 2014, an ice storm caused an outage which lasted for 38 hours and 10 minutes and affected a significant number of PECO customers, including Mr. Rounce.  Tr. 83, PECO Exhibit 1.

14.	On February 12, 2014, an outage resulted from an underground fault of PECO’s equipment and lasted nine hours and 52 minutes affecting 69 customers, including Mr. Rounce.  Tr. 82, PECO Exhibit 1.

15.	An “underground fault” outage can occur for a variety of reasons including degradation of  the cable insulation due to manufacturing issues, failed connection points (such as a splice that an underground repairman has put into the cable), current magnitude exceeding the rating of the equipment, or someone digging into an underground cable.  Tr. 74, 128.

16.	PECO has implemented a cable injection program for a particular type of cable that the Company has identified as having a type of insulation that is prone to degradation.  Tr. 75.

17.	PECO’s cable injection program identifies the problematic sections and rebuilds the insulation.  Id.

18.	On June 30, 2014, a possible lightning strike caused a utility pole to catch fire, resulting in a 16 minute outage for 1,949 PECO customers, including Mr. Rounce.  Tr. 81-82, PECO Exhibit 1.

19.	On July 2, 2014, a possible lightning strike burned wires and caused a one hour and 12 minute outage for 2,315 PECO customers, including Mr. Rounce.  Tr. 81, PECO Exhibit 1.

20.	On July 8, 2014, a tree growth pulled primary wires down causing an outage which lasted 16 hours and 6 minutes and affected 293 customers, including Mr. Rounce.  Tr. 79-80, PECO Exhibit 1.

21.	On July 28, 2014, a tree came into contact with PECO’s primary facilities resulting in an outage which lasted one hour and 43 minutes and affected 294 customers, including Mr. Rounce.  Tr. 79, PECO Exhibit 1.

22.	On September 1, 2014, a tree limb caused an outage that lasted one hour and 37 minutes and affected 1,144 customers, including Mr. Rounce.  Tr. 79, PECO Exhibit 1.

23.	On September 13, 2014, a fallen tree limb caused an outage that lasted one hour and two minutes and affected 1,144 customers, including Mr. Rounce.  Tr. 79, PECO Exhibit 1.

24.	On November 2, 2014, a tree limb fell on primary wires causing an outage which lasted for five hours and 13 minutes, and affected 2,884 customers, including Mr. Rounce.  Tr. 77-78, PECO Exhibit 1.

25.	On June 12, 2015, a vehicle hit a utility pole resulting in an outage which lasted one hour and 25 minutes and affected 1,153 customers, including Mr. Rounce.  Tr. 71, PECO Exhibit 1.

26.	On June 20, 2015, an underground cable fault caused an outage isolated to Mr. Rounce’s development.  It affected 69 customers and lasted nine hours and 28 minutes.  Tr. 74, PECO Exhibit 1.

27.	On June 23, 2015, a storm resulted in an outage which lasted 24 hours and 51 minutes, and affected 40,000 PECO customers within the Delaware and Chester Counties, including Mr. Rounce.  Tr. 71-72, PECO Exhibit 1.

28.	On July 4, 2015, a vehicle hit a utility pole resulting in an outage which lasted 31 minutes, and affected 1,958 customers, including Mr. Rounce.  Tr. 71, PECO Exhibit 1.

29.	On July 11, 2015, an uprooted tree caused an outage which lasted 50 minutes and affected 1,301 customers, including Mr. Rounce.  Tr. 72, PECO Exhibit 1.

30.	Momentary outages are typically the result of PECO’s recloser devices.  Tr. 66, 84.

31.	Reclosers are similar to circuit breakers and operate to isolate a fault on overvoltage or overcurrent.  Tr. 66.

32.	One of the purposes of the reclosers is to prevent sustained outages.  Tr. 66.

33.	PECO employs recloser devices in its circuits programing them to restore power to as many customers as possible, typically within 60 seconds.  Tr. 66, 123.

34.	PECO considers the installation of reclosers a reliability enhancement measure, which impacts PECO’s System Average Interruption Frequency Index (SAIFI) as well as its Customer Average Interruption Duration Index (CAIDI).  Tr. 67, 123.

35.	Top Priority Circuit (TPC) is PECO’s reliability program aimed to address the top 10 percent of the circuits that are determined to be poor performers based on data from SAIFI and CAIDI.  Tr. 87, see also 118, 135.

36.	Following an in-depth reliability analysis of the SAIFI and CAIDI figures for the year 2010, PECO included the Middleton 352 circuit in its TPC for the year 2011.  Tr. 90, 119.

37.	As part of the TPC program for the year 2011, PECO performed targeted tree trimming and installed more switches in the Middletown 352 circuit.  Tr. 90, PECO Exhibit 1.

38.	In April of 2011, PECO installed a recloser in the Middleton 352 circuit.  Tr. 90, PECO Exhibit 1.

39.	In January of 2012, the Middleton 352 circuit was reconfigured and a portion of the power was redirected to another source.  Tr. 89, PECO Exhibit 1.

40.	As part of the January 2012 project, PECO installed a recloser which helps isolate some of the aerial portions of the Middleton 352 circuit so that any vegetation issues on that stretch of the circuit have less or no impact on Mr. Rounce’s service.  Tr. 90, PECO Exhibit 1.

41.	In January 2014, PECO upgraded a recloser in the Middleton 352 circuit to a newer model.  Tr. 88, 125-26, PECO Exhibit 1.

42.	In April 2015 and August 2015, PECO upgraded two more reclosers in the Middleton 352 circuit to newer models.  Tr. 88, 125-26, PECO Exhibit 1.

43.	In May of 2014, PECO performed targeted tree trimming in the vicinity of 3430 North Providence Road, on the aerial portion of Mr. Rounce’s circuit.  Tr. 89, PECO Exhibit 1.

44.	Following an in-depth reliability analysis of the SAIFI and CAIDI figures for the year 2014, PECO included the Middleton 352 circuit in its TPC for the year 2015.  Tr. 87, 118.

45.	As part of the 2015 TPC program, PECO reconfigured the recloser scheme of Middletown 352 to improve service reliability.  Tr. 87, 126.

46.	In August of 2015, two reclosers located on Bishop Hollow Road were reconfigured to isolate any outage occurring on that stretch of the circuit.  Tr. 87-88, PECO Exhibit 1.

47.	PECO has contracted with a third party to patrol annually every aerial facility on the PECO system.  Tr. 90-91, PECO Exhibit 1.

48.	The annual circuit patrol involves a visual inspection for defects as well as a thermography inspection for any hot spots outside of normal operating temperatures.  Tr. 91, 157-58, PECO Exhibit 1.

49.	The purpose of the annual circuit patrol is to identify potential problems and prevent outages before they occur.  Tr. 91.

50.	The last circuit patrol on Middletown 352 occurred on April 20, 2015.  Tr. 91, PECO Exhibit 16.

51.	Power outages are primarily reported to PECO through customers calling the Company to report the outage.  Tr. 64.

52.	PECO’s AMI meters are able to report to its outage management system that they have lost power; however, PECO still requires that customers call in to report the outage in order to confirm the information received from the AMI meters.  Tr. 64, 69.

53.	Power spikes are very short pulses of energy on a power line.  Tr. 20-21, 59, Complainant Exhibit 2.

54.	Power spikes contain very high voltages, but usually last only a few milliseconds.  Tr. 20-21, 59, Complainant Exhibit 2.

55.	A power surge, or transient, is a temporary increase in voltage on a power line.  Tr. 20-21, Complainant Exhibit 2.

56.	Power surges typically have less voltage than power spikes but last longer.  Tr. 20-21, Complainant Exhibit 2.

57.	Electric appliances will break down if exposed to power spikes or surges over a long period of time.  Tr. 23.

58.	Flickering lights can be caused by any voltage transient, like a microwave or a heat pump turning on and off.  Tr. 107.

59.	On October 20, 2012, Mr. Rounce sent a letter to PECO complaining about surges, voltage, spike, voltage drops, brownouts and service outages he had experienced while residing at the Service Address.  Tr. 50, Complainant Exhibit 6.

60.	On March 1, 2013, PECO installed a recording volt meter (RVM) in Complainant’s house.  Tr. 110-11, PECO Exhibit 5.

61.	The RVM is attached to the service wire of a property for a certain period of time for the purpose of monitoring and recording voltage and current into and out of the property.  Tr. 110-11.

62.	Once the RVM is installed, PECO is able to obtain actual current and voltage data, as well as root mean square (RMS) voltage and current data from the device.  Tr. 112-13.

63.	The RMS is an average of voltage and current data over a certain period of time.  Tr. 113.

64.	PECO’s RVM remained in Mr. Rounce’s residence for 10 days.  Tr. 113.

65.	The records obtained from the RVM upon its removal from the Complainant’s residence indicated that the voltage had stayed within the limits permitted by Commission regulation.  Tr. 113, 118, PECO Exhibit 5.

66.	The records obtained from the RVM upon its removal from the Complainant’s residence indicated that voltage at the Service Address was influenced only by the load on the customer’s line.  Tr. 113, 116-18, PECO Exhibit 5.

67.	Following the filing of the present Complaint, Mr. Rounce declined PECO’s offer to conduct another voltage testing at the Service Address.  Tr. 114-15.

Safety

68.	On August 29, 2015, residents of Wilton Woods Lane experienced a power outage caused by an underground cable fault.  Tr. 97.

69.	The Company isolated the faulty cable and installed a temporary one to restore power to its customers until permanent repairs were made.  Tr. 98, PECO Exhibits 3 and 4.

70.	The temporary cable was a 2,400 volt line that was a fully insulated and the portion of it crossing the local road was covered by a cable raise to protect it from oncoming traffic.  Tr. 98-99, 130, Complainant Exhibit 3, PECO Exhibit 4.

71.	The elbow connection from cable to transformer was covered and the only bare conductor at the scene was the neutral wire which is grounded at zero volts.  Tr. 133-34, Complainant Exhibit 3, PECO Exhibit 4.

72.	PECO tags temporary high voltage cables every 10 to 20 feet to indicate their nature.  Tr. 101, 104.

73.	If repairs involve excavation, PECO protects and marks the site with ropes and cones and places plywood over the hole.  Tr. 101, 104.

74.	PECO determined that the August 29, 2015 outage was caused by 725 feet of faulty underground cable, which needed to be replaced.  Tr. 101-103, PECO Exhibit 3.

75.	A PECO contractor had to come and perform the necessary installation. Tr. 101-103, PECO Exhibit 3.

76.	The temporary cable remained on site for 81 days following the August 29, 2015 outage.  Tr. 101.

77.	PECO received no reports of accidents related to the cable work performed on Wilton Woods Lane between August and November 2015.  Tr. 104.

78.	Mr. Rounce’s service was not affected by the power outage on August 29, 2015, or the cable replacement work that followed.  Tr. 94-97, PECO Exhibit 2.

Vegetation

79.	PECO has set in place reliability based programs in vegetation management.  Tr. 145.

80.	The Middletown 352 circuit has been scheduled frequently in PECO’s reliability based programs due to the tree-related outages over the years.  Tr. 145.

81.	Before January 2016, PECO had a five-year tree-trimming cycle for all of its circuits.  Tr. 144-154.

82.	Beginning in January 2016, PECO placed all of its 34 kV circuits on a three-year maintenance cycle.  Tr. 144, 154.

83.	On March 28, 2011, a PECO field investigator patrolled the Middletown 352 circuit looking for problematic areas of vegetation growth.  Tr. 148, PECO Exhibit 6.

84.	The vegetation maintenance work on the Middletown 352 circuit was completed on April 29, 2011.  Id.

85.	On October 10, 2012, the vegetation around the Middletown 352 circuit was inspected again, as part of PECO’s reliability based program.  Tr. 149, PECO Exhibit 6.

86.	On November 12, 2013, PECO performed a mid-cycle tree trimming on the Middletown 352 circuit again as part of the Company’s reliability based program.  Tr. 149-50, 154, PECO Exhibit 6.

87.	The last tree trimming on Mr. Rounce’s circuit was performed on January 2015.  Tr. 144, 151-53, PECO Exhibits 1 and 7.

DISCUSSION

In his formal Complaint, Mr. Rounce alleged that he was having a reliability, safety or quality problem with his electricity service.  In particular, Mr. Rounce averred that in his 30 years as a PECO customer he has experienced problems with numerous outages, surges, spikes and brownouts, which have persisted despite his complaints to PECO.  As relief, Mr. Rounce requested that the Commission conduct independent testing and investigate the surges, spikes and brownouts that occur on the PECO line on which his house is located.

As the proponent of a rule or order, the Complainant in this proceeding bears the burden of proof pursuant to Section 332(a) of the Public Utility Code (Code), 66 Pa.C.S.A. § 332(a).  To satisfy this burden, the Complainant must demonstrate that the Respondent was responsible for the problems alleged in the Complaint through a violation of the Code or a regulation or order of the Commission.  This must be shown by a preponderance of the evidence.  Patterson v. Bell Telephone Company of Pennsylvania, 72 Pa. PUC 196 (1990).  Preponderance of the evidence means that the party with the burden of proof has presented evidence that is more convincing than that presented by the other party.  Samuel J. Lansberry, Inc. v. Pa. Pub. Util. Comm’n, 578 A.2d 600 (Pa.Cmwlth. 1990) alloc. den., 602 A.2d 863 (Pa.1992).  In addition, the Commission’s decision must be supported by “substantial evidence,” which consists of evidence that a reasonable mind might accept as adequate to support a conclusion.  A mere “trace of evidence or a suspicion of the existence of a fact” is insufficient.  Norfolk and Western Railway Co. v. Pa. Pub. Util. Comm’n, 413 A.2d 1037 (Pa.1980).

Upon the presentation by the Complainant of evidence sufficient to initially satisfy the burden of proof, the burden of going forward with the evidence to rebut the evidence of the Complainant shifts to the Respondent.  If the evidence presented by the Respondent is of co-equal weight, the Complainant has not satisfied her burden of proof.  The Complainant would be required to provide additional evidence to rebut the evidence of the Respondent.  Burleson v. Pa. Pub. Util. Comm’n, 443 A.2d 1373 (Pa.Cmwlth. 1982), aff'd, 461 A.2d 1234 (Pa.1983).

While the burden of persuasion may shift back and forth during a proceeding, the burden of proof never shifts.  The burden of proof always remains on the party seeking affirmative relief from the Commission.  Milkie v. Pa. Pub. Util. Comm’n, 768 A.2d 1217 (Pa.Cmwlth. 2001).

Complainant’s Testimony

- Outages, Spikes and Surges

At the evidentiary hearing, Mr. Rounce testified that he has a degree in electrical engineering, a degree in environmental engineering, and another one in business.  Tr. 52-53.  He worked for General Electric Company in the power system division as a design engineer for high voltage transmission lines.  Tr. 53.  Later, he was Vice President of marketing for Biddle Instruments, which manufactures equipment designed to find cable faults and perform insulation testing.  Tr. 53.

Mr. Rounce testified that he has been a long-time customer of PECO and its predecessor.  Tr. 9.  He stated that since 1985 he has experienced a constant pattern of outages, spike transients, and service problems with the Company.  Mr. Rounce defined power spikes as very short pulses of energy on a power line.  They contain very high voltages but usually last only a few milliseconds.  Tr. 20-21, 59, Complainant Exhibit 2.  A power surge or transient is a temporary increase in voltage on a power line.  Tr. 20-21, Complainant Exhibit 2.  Mr. Rounce explained that surges typically have less voltage than power spikes but last longer.  Tr. 20-21, Complainant Exhibit 2.  According to Mr. Rounce, over a long period of time spikes and surges will destroy electric appliances.  Tr. 23.

He testified that over the last 30 years he has had several appliances destroyed by high voltage, spikes or transients on his line.  Tr. 20-22, 54-55, Complainant Exhibit 2.  Apart from that, he says that his lights flicker, the motor of his heat pump groans when it starts after an outage, sparks and brown marks are all over the insides of the heat pump, and his computer has lost data as spikes go through hard drives and sectors get misappropriated.  Tr. 54, 56.

Mr. Rounce states that he has installed suppression systems in his residence to protect his electric appliances, equipment and data from the damages caused by spikes and surges.  Tr. 22, 51-52.  This, he states, has minimized the problem, but has not resolved it.  Tr. 23.  He believes that the spikes and surges are the result of the Company shifting loads, or balancing generation with distribution by bringing on additional capacity.  Tr. 22-23.  According to Mr. Rounce, PECO is shifting loads without having protective systems in place.  Tr. 23, 25.  He testified that he does not believe that PECO’s service meets the Commission’s standards for reliability and quality of electric service.  Tr. 36.  He has not done any testing or measuring of voltage or current inside the Service Address himself.  Tr. 53-54.

Mr. Rounce testified that after an outage he has to reset all the clocks in the house.  Tr. 57.  He has used this practice to record the duration of outages, both sustained and momentary, through the years.  Tr. 57.  From 2010 to 2015, he recorded the following outages:

| Year | Number of Outages | Total Hours Off |
| --- | --- | --- |
| 2010 | 8 | 48.6 |
| 2011 | 5 | 5.1 |
| 2012 | 6 | 22.5 |
| 2013 | - | - |
| 2014 | 15 | 75.15 |
| 2015 | 5 | 39 |

Complainant Exhibit 1.

Mr. Rounce testified that the outages have caused him an inconvenience and have cost him money.  Tr. 55.  He stated that he has lost a lot of data from his business as a result of these outages.  Tr. 55-56.

Mr. Rounce testified that whenever there is a power outage, PECO is not aware of it unless and until the customers experiencing the outage call PECO to report it.  Tr. 35.  According to the Complainant, in the year 2016, PECO should not need to rely on its customers to report a power outage.  Id.  He pointed out that some of these power outages are so long that the customers lose phone service.  Tr. 35.

During cross-examination, Mr. Rounce testified that surges and spikes are a constant phenomenon in PECO’s line, and that any engineer with an oscilloscope can monitor the lines and see these spikes.  Tr. 47.  Yet, Mr. Rounce expressed distrust of the results of PECO’s RVM which found voltage in Mr. Rounce’s residence to be within the allowable limits in March of 2013.  Tr. 50.  According to Mr. Rounce, PECO’s equipment, the RVM, was not sophisticated enough to detect the spikes.  Tr. 50.

- Safety

Mr. Rounce testified that he had occasion to witness PECO laying a high voltage power cable above ground creating an unsafe condition in his neighborhood.  Tr. 27, 29.  He stated that the high voltage cable and other PECO underground equipment remained exposed for 81 days following a service outage on August 29, 2015.  Tr. 27-30, 45-46.  He believes that PECO is creating unsafe conditions, which then result in power spikes, surges and outages and affect PECO’s reliability, and vice versa.  Tr. 30.

- Vegetation

Mr. Rounce testified that his service line is fed by a 34 kV circuit known as Middletown 352, which runs along PA Route 352.  Tr. 41.  He acknowledged that although the power lines within his development are underground, the main portion of Middletown 352 consists of aerial lines.  Tr. 56.  Despite this, he insists that vegetation and weather are not the cause of the outages.  Tr. 56.  In support of his argument, Mr. Rounce pointed out that oftentimes, people who reside in the area between PA Route 352 and his development have electricity while his service is out.  Tr. 14, 41-43.  He also noted that that there is no historical correlation between the weather and the outages.  Tr. 12, 24.

When asked about the relief he sought from the Commission, Mr. Rounce explained that he sought a solution to the service reliability problem that he is experiencing as a PECO customer.  Tr. 13.  He wants PECO to put in place recloser systems that are necessary to stop the outages and transients on his line.  Tr. 13, 39-40.  In addition, he wants PECO to submit a clear plan and a time frame for reporting progress to the Commission.  Tr. 13, 39-40.  While Mr. Rounce does not believe that PECO is doing this purposefully, he believes that the present Complaint will call attention to the service reliability problem that he has experienced in the last 30 years.  Tr. 40.

Respondent’s Testimony

- Outages, Spikes and Surges

In response to Mr Rounce’s testimony on safety and reliability of service, PECO’s witness, Nathaniel Nichols explained that Mr. Rounce’s residence is fed from a 34,000 volt line, identified as “Middletown 352.”  From PECO’s Middletown substation, fully insulated aerial cable extends for approximately three miles before it transitions to open aerial wires.  These are the bare conductors typically found on top of a pole.  Tr. 67-68.  They extend down Providence Road, past the entrance to Mr. Rounce’s development where the aerial cable is then connected to underground wire.  The underground wire extends along East Deerfield Drive, goes to Forest Lake Drive and then to Mr. Rounce’s home.  Tr. 68.  Because the power supply from PECO’s substation to the development where Mr. Rounce’s house is located includes aerial facilities, power at the Service Address is susceptible to tree-related incidents.  Tr. 68.

In particular, Mr. Nichols testified that from January 1, 2011 to January 1, 2016, PECO recorded 18 sustained outages affecting Mr. Rounce’s service.  Tr. 69, PECO Exhibit 1.

In 2011, PECO recorded one sustained outage, which occurred on February 2, 2011.  It was caused by tree growth coming into contact with primary wires, lasted for six hours and eight minutes and affected 1,301 PECO customers, including Mr. Rounce.  Tr. 86, PECO Exhibit 1.

In 2012, PECO recorded two sustained outages affecting Mr. Rounce’s service.  Tr. 85, PECO Exhibit 1.  The first one occurred on April 30, 2012, when a contractor hired by a neighbor of Mr. Rounce inadvertently hit PECO’s underground secondary wire as he was replacing the neighbor’s driveway.  The incident caused PECO’s transformer to trip off and resulted in an outage, which lasted for two hours and 33 minutes.  The outage affected only seven customers, including Mr. Rounce.  Tr. 85-86, PECO Exhibit 1.  The second outage occurred on October 29, 2012, when a broken tree limb or trunk fell on PECO’s equipment causing an outage which lasted one hour and 13 minutes and affected 294 customers, including Mr. Rounce.  Tr. 85, PECO Exhibit 1.

In 2013, PECO recorded one sustained outage, which was caused by a tree limb coming into contact with primary wires.  The outage lasted 53 minutes and affected 294 customers, including Mr. Rounce.  Tr. 85, PECO Exhibit 1.

In 2014, PECO recorded nine sustained outages affecting Mr. Rounce’s service:  five of the outages were caused by vegetation, two were related to weather events, one was related to a pole fire possibly caused by lightning, and one was related to an underground cable fault.  Tr. 77, PECO Exhibit 1.

On February 5, 2014, an ice storm caused an outage affecting a significant number of PECO customers, including Mr. Rounce.  It lasted for 38 hours and 10 minutes.  Mr. Nichols explained that PECO referred to this storm as “the ice crusher” and the Company had to call in crews from out of state to assist with the restoration of service after that storm.  Tr. 83.

On February 12, 2014, an outage resulted from underground fault of PECO equipment.  It lasted nine hours and 52 minutes and affected 69 customers, including Mr. Rounce.  Tr. 82.

On June 30, 2014, a possible lightning strike caused a utility pole to catch fire, resulting in a 16 minute outage for 1,949 PECO customers, including Mr. Rounce.  Tr. 81-82, PECO Exhibit 1.

On July 2, 2014, a possible lightning strike burned wires and caused a one hour and 12 minute outage for 2,315 PECO customers, including Mr. Rounce.  Tr. 81.

On July 8, 2014, a tree growth pulled primary wires down causing an outage which affected 293 customers, including Mr. Rounce, and lasted 16 hours and 6 minutes.  Tr. 79-80.  PECO had to reassemble the wires and put them back up onto the poles.  Id.

On July 28, 2014, a tree came into contact with PECO’s primary facilities.  The resulting outage affected 294 customers, including Mr. Rounce, and lasted one hour and 43 minutes.  Tr. 79.

On September 1, 2014, a tree limb caused an outage that lasted one hour and 37 minutes and affected 1,144 customers, including Mr. Rounce.  Tr. 79.

On September 13, 2014, a fallen tree limb caused an outage that lasted one hour and two minutes and affected 1,144 customers, including Mr. Rounce.  Tr. 79.

On November 2, 2014, a tree limb fell on primary wires causing an outage which lasted for five hours and 13 minutes, and affected 2,884 customers, including Mr. Rounce.  Tr. 77-78.

Mr. Nichols testified that in 2015, PECO recorded five sustained outages affecting Mr. Rounce’s service:  two of the outages were caused by vegetation, one by an equipment failure, and two were the result of public damage where vehicles hit PECO’s utility poles.  Tr. 69-70, 74, PECO Exhibit 1.

The first public damage incident occurred on June 12, 2015, and affected 1,153 customers, including Mr. Rounce.  The resulting outage lasted one hour and 25 minutes.  Tr. 71.  The second public damage incident occurred on July 4, 2015, and affected 1,958 customers including Mr. Rounce.  The resulting outage lasted 31 minutes.  Tr. 71.

The equipment-related outage occurred on June 20, 2015.  It resulted from an “underground fault” specific to Mr. Rounce’s development.  It affected 69 customers and lasted nine hours and 28 minutes.  Tr. 74.  Mr. Nichols testified that an “underground fault” outage can occur for a variety of reasons including degradation of  the cable insulation due to manufacturing issues, failed connection points (such as a splice that an underground repairman has put into the cable), current magnitude exceeding the rating of the equipment, or someone digging into an underground cable.  Tr. 74, 128.  He explained that PECO has implemented a cable injection program for a particular type of cable that the Company has identified as having a type of insulation that is prone to degradation.  PECO’s cable injection program identifies the problematic sections and rebuilds the insulation.  Tr. 75.

The first vegetation incident occurred on June 23, 2015, and was the result of a storm, which affected 40,000 PECO customers within the Delaware and Chester Counties, including Mr. Rounce.  The resulting outage lasted 24 hours and 51 minutes.  Tr. 71-72.  The second vegetation incident occurred on July 11, 2015, and involved an uprooted tree.  The resulting outage affected 1,301 customers, including Mr. Rounce, and lasted 50 minutes.  Tr. 72.

Mr. Nichols explained that the 18 outages listed in his testimony and in PECO’s Exhibit 1 were sustained outages more than five minutes in duration, which Mr. Nichols distinguished from momentary outages which last less than five minutes.  Tr. 65.  Mr. Nichols further explained that momentary outages occur for a variety of reasons, but in the circuit which feeds Mr. Rounce’s line momentary outages are typically the result of PECO’s recloser devices.  Tr. 66, 84.  Mr. Nichols described reclosers as being very similar to circuit breakers because they operate to isolate a fault on overvoltage or overcurrent.  Tr. 66.  They can also operate when they sense that there is no power supply to them.  Tr. 66.  In cases of power outages, these recloser devices  will operate to restore power to as many PECO customers as possible, typically within 60 seconds.  Tr. 66.  One of the purposes of these reclosers is to prevent sustained outages.  Tr. 66, 123.  PECO considers the installation of reclosers a reliability enhancement measure, which impacts PECO’s System Average Interruption Frequency Index (SAIFI) as well as its Customer Average Interruption Duration Index (CAIDI).  Tr. 67, 123.

Mr. Nichols testified at length with regard to the reliability enhancement measures that PECO has taken in order to address the service outages experienced by its customers connected to Middletown 352 circuit.  He explained that Top Priority Circuit (TPC) is PECO’s reliability program aimed to address the top 10 percent of the circuits that are determined to be poor performers based on data from SAIFI and CAIDI.  Tr. 87, see also 118, 135.  Mr. Nichols stated that following an in-depth reliability analysis of the SAIFI and CAIDI figures for the year 2010, PECO included the Middleton 352 circuit in its TPC for the year 2011.  Tr. 90, 119.

As part of the TPC program, PECO performed targeted tree trimming and installed more switches in the system.  Tr. 90.  In particular in April of 2011, PECO installed a recloser in the Middleton 352 circuit.  Tr. 90.  In January of 2012, PECO’s central engineering department determined that the Middleton 352 circuit was feeding a substantial amount of load.  The forecast on that circuit was projecting that the load would begin to exceed emergency readings or normal ratings on that circuit.  Tr. 89.  So the circuit itself was reconfigured and a portion of the power was redirected to another source.  Id.  As part of the January 2012 project, PECO installed a recloser, which helps isolate some of the aerial portions of the Middleton 352 circuit so that any vegetation issues on that stretch of the circuit have less or no impact on Mr. Rounce’s service. Tr. 90.  In May of 2014, PECO performed targeted tree trimming in the vicinity of 3430 North Providence Road, on the aerial portion of Mr. Rounce’s circuit.  Tr. 89.  In January 2014, April 2015 and August 2015, PECO upgraded three reclosers in Mr. Rounce’s circuit to newer models.  Tr. 88, 125-26.

Following an in-depth reliability analysis of the SAIFI and CAIDI figures for the year 2014, PECO included the Middleton 352 circuit in its TPC for the year 2015.  Tr. 87, 118.  As part of the TPC program, PECO reconfigured the recloser scheme of Middletown 352 in August of 2015 to improve service reliability.  Tr. 87, 126.  Two reclosers located on Bishop Hollow Road were reconfigured to isolate any outage occurring on that stretch of the circuit.  Tr. 87-88.

Mr. Nichols testified that, in addition to reliability enhancement measures, PECO has also conducted preventive maintenance work on the Middletown 352 circuit.  He explained that PECO has contracted with a third party to patrol annually every aerial facility on the PECO system.  Tr. 90-91, PECO Exhibit 1.  The circuit patrol involves a visual inspection for defects as well as a thermography inspection for any hot spots outside of normal operating temperatures.  Tr. 91, 157-58, PECO Exhibit 1.  The purpose of the annual circuit patrol is to identify potential problems and prevent outages before they occur.  Tr. 91.  According to Mr. Nichols the last circuit patrol on Middletown 352 occurred on April 20, 2015.  Tr. 91, PECO Exhibit 16.  The next circuit patrol is scheduled for 2016.  Id.

Mr. Nichols testified that outages are primarily reported to PECO through customers calling the Company and reporting the outage.  Tr. 64.  He explained that the recently deployed AMI meters are also able to report to PECO’s outage management system that they have lost power.  Tr. 64.  Yet, he stated that PECO still requests that customers call in to report the outage in order to confirm the information received from the AMI meters.  Tr. 69.

Mr. Nichols next addressed Mr. Rounce’s claim of surges and spikes on his line.  Mr. Nichols agreed with Mr. Rounce’s definition of surges and spikes, and with Mr. Rounce’s statement that spikes, surges, and brownouts can affect the life of electric appliances.  Tr. 130.  He clarified that in most cases, a power surge would cause a fuse to blow and isolate the issue.  Tr. 105-106, 120.  He also added that flickering lights can be caused by any voltage transient, like a microwave or a heat pump turning on and off.  Tr. 107.  However, he maintained that flickering lights caused by the operation of customer’s appliances is not a reflection of the quality of PECO’s service.  Tr. 108.

Mr. Nichols testified that on October 20, 2012, Mr. Rounce sent a letter to PECO complaining about surges, voltage, spike, voltage drops, brownouts and service outages he had experienced while residing at the Service Address.  Tr. 50, Complainant Exhibit 6.  On March 1, 2013, PECO installed a recording volt meter (RVM) in Complainant’s house following Mr. Rounce’s complaint of “dirty power.”  Tr. 110-11, PECO Exhibit 5.  Mr. Nichols explained that the RVM is attached to the service wire of a property for a certain period of time for the purpose of monitoring and recording voltage and current into and out of the property.  Tr. 110-11.  Once the RVM is set, PECO is able to obtain actual current and voltage data, as well as root mean square (RMS) voltage and current data from the device.  Tr. 112-13.  The RMS is an average of the data over a certain period of time.  Tr. 113.  PECO’s RVM remained in Mr. Rounce’s residence for 10 days.  Tr. 113.  The records obtained from the RVM upon its removal from the Complainant’s residence indicated that the voltage had stayed within the limits permitted by Commission regulation.  Tr. 113, 118, PECO Exhibit 5.  In addition, the records obtained from the RVM indicated that voltage at the Service Address was influenced only by the load on the customer’s line, specifically the two heat pumps that were still in operation in early March of 2013.  Tr. 113, 116-18, PECO Exhibit 5.  Mr. Nichols further testified that, following the filing of the present Complaint, PECO offered to conduct another voltage testing at Mr. Rounce’s residence.  That offer was declined by the Complainant.  Tr. 114-15.

Finally, Mr. Nichols addressed Mr. Rounce’s claim of load shifting on the part of PECO.  Mr. Nichols explained that capacity to meet demand can be the cause of spikes and surges, but only in extreme circumstances.  Tr. 109.  He added that PECO had reviewed Mr. Rounce’s circuit and his service and did not detect any issue with load switching affecting his service.  Tr. 105.

- Safety

Mr. Nichols testified that on August 29, 2015, residents of Wilton Woods Lane experienced a power outage caused by an underground cable fault.  Tr. 97.  The Company isolated the faulty cable and installed a temporary one to restore power to its customers until permanent repairs were made.  Tr. 98, PECO Exhibits 3 and 4.  The temporary cable was a 2,400 volt line that was fully insulated, and the portion of it crossing the local road was covered by a cable raise to protect it from oncoming traffic.  Tr. 98-99, 130, Complainant Exhibit 3, PECO Exhibit 4.  The elbow connection from cable to transformer was covered.  Tr. 133-34, Complainant Exhibit 3, PECO Exhibit 4.  The only bare conductor at the scene was the neutral wire which is grounded at zero volts.  Tr. 134, Complainant Exhibit 3, PECO Exhibit 4.

Mr. Nichols explained that PECO tags temporary high voltage cables every 10 to 20 feet to indicate their nature.  Tr. 101, 104.  If repairs involve excavation, the site is protected and marked with ropes and cones, and plywood is placed over the hole.  Tr. 101, 104.

With regard to the August 29, 2015 outage, Mr. Nichols explained that PECO determined that 725 feet of faulty cable needed to be replaced altogether, instead of simply being repaired.  A PECO contractor had to come and perform the necessary installation. Tr. 101-103, PECO Exhibit 3.  The temporary cable remained on site for 81 days following the August 29, 2015 outage.  Tr. 101.  Mr. Rounce’s service was not affected by the power outage on August 29, 2015, or by the cable replacement work that followed.  The work was done on Wilton Woods Lane.  Mr. Rounce’s residence is located on a different street, Forest Lake Drive, and is powered by a different transformer than the one powering Wilton Woods Lane.  Tr. 94-97, PECO Exhibit 2.  PECO received no reports of accidents related to the cable work performed on Wilton Woods Lane between August and November 2015.  Tr. 104.

- Vegetation

Mr. Jeffrey Watson testified as PECO’s senior vegetation manager.  He explained that PECO has set in place reliability based programs in vegetation management.  Tr. 145.  The Middletown 352 circuit has been scheduled frequently in PECO’s reliability based programs due to the tree-related outages over the years.  Tr. 145.

Mr. Watson reiterated Mr. Nichols’ description of the Middletown 352 circuit as having approximately 20 miles of aerial primary cable, which renders it susceptible to vegetation-related issues.  Tr. 146.  Mr. Watson testified that, in order to address those issues, PECO performs preventive maintenance on the circuit.  Tr. 143.  PECO looks for dead canopy above the lines, or tree limbs and trunks that are too close to the primary wires, and prunes the trees accordingly.  Tr. 144.

Mr. Watson explained that before January 2016, PECO had a five-year tree-trimming cycle for all its circuits.  Tr. 144-154.  However, beginning in January 2016, PECO placed all of its 34 kV circuits on a three-year maintenance cycle.  Tr. 144, 154.

As part of the old vegetation maintenance cycle for the 34 kV circuit, a PECO field investigator patrolled the Middletown 352 circuit on March 28, 2011, looking for problematic areas of vegetation growth.  Tr. 148, PECO Exhibit 6.  The vegetation maintenance work on the Middletown 352 circuit was completed on April 29, 2011.  Id.  The vegetation around the Middletown 352 circuit was inspected again on October 10, 2012, as part of PECO’s reliability based program.  Tr. 149, PECO Exhibit 6.  On November 12, 2013, PECO performed a mid-cycle tree trimming on the Middletown 352 circuit again as part of the Company’s reliability based program.  Tr. 149-50, 154, PECO Exhibit 6.  The last tree trimming on Mr. Rounce’s circuit was performed on January 2015 as part of PECO’s five-year cycle.  Tr. 144, 151-53, PECO Exhibits 1 and 7.

Disposition

Section 1501 of the Public Utility Code states as follows in pertinent part:

§ 1501. Character of service and facilities

Every public utility shall furnish and maintain adequate, efficient, safe, and reasonable service and facilities, and shall make all such repairs, changes, alterations, substitutions, extensions, and improvements in or to such service and facilities as shall be necessary or proper for the accommodation, convenience, and safety of its patrons, employees and the public. Such service also shall be reasonably continuous and without unreasonable interruptions or delay. Such service and facilities shall be in conformity with the regulations and orders of the commission. Subject to the provisions of this part and the regulations or orders of the commission, every public utility may have reasonable rules and regulations governing the condition under which it shall be required to render service.

66 Pa. C.S.A § 1501 (Emphasis added).  A public utility is not obligated to provide perfect service and facilities 100% of the time.  A-Rize-N Management Co. LLC v. Pennsylvania American Water Co., Docket No. C-2009-2119162 (Order entered June 15, 2010).

Service rules and regulations adopted by public utilities relating to rates and service are known as “tariffs”; tariffs filed with state regulatory agencies such as the public utility commission are not mere contracts but have the force of law and are binding on the consumer and the utility.  Stiteler v. Bell Telephone Company, 379 A.2d 339 (Pa.Cmwlth. 1977); Brockway Glass Company v. Pennsylvania Public Utility Commission, 437 A.2d 1067 (Pa.Cmwlth. 1981); Pennsylvania Electric Company v. Pennsylvania Public Utility Commission, 663 A.2d 281 (Pa.Cmwlth. 1995).

PECO’s tariff provisions cover outages, surges and spikes.  Respondent’s Tariff Rule 12 provides as follows in pertinent part:

12. SERVICE CONTINUITY

12.1 LIMITATION ON LIABILITY FOR SERVICE INTERRUPTIONS AND VARIATIONS. The Company does not guarantee continuous, regular and uninterrupted supply of service. The Company may, without liability, interrupt or limit the supply of service for the purpose of making repairs, changes, or improvements in any part of its system for the general good of the service or the safety of the public or for the purpose of preventing or limiting any actual or threatened instability or disturbance of the system. The Company is also not liable for any damages due to accident, strike, storm, riot, fire, flood, legal process, state or municipal interference, or any other cause beyond the Company's control.

PECO Energy Company – Supplement No. 15 to Tariff Electric PA. P.U.C. No. 5, Original Page No. 4, Effective January 1, 2010.  (Emphasis added).

In addition, Chapter 57, Subchapter B of the Commission regulations sets forth service and facilities standards. 52 Pa.Code §§ 57.11 to 57.27. The standards pertaining to voltage provide as follows:

§ 57.14. Service voltage.
 
(a) Standard voltage. A public utility shall adopt a standard nominal service voltage for the entire territory served by the public utility, and shall file with the Commission data on such standard service voltage or voltages as part of its officially filed tariff. The suitability and adequacy of the standard nominal service voltage or voltages adopted may be determined at any time by the Commission.
 
(b) Allowable voltage variation (primarily lighting). For service rendered primarily for lighting purposes, the allowable variation in voltage measured at the service terminals of the customer may not exceed, for a longer period than 1 minute in each instance, 5%

above or below the standard nominal service voltage and a total variation from minimum to maximum of 8% during normal system operation.
 
(c) Allowable voltage variation (primarily power). For service rendered primarily for power purposes, the allowable variation in voltage measured at the service terminals of the customer may not exceed, for a longer period than 1 minute in each instance, 10% above or below the standard nominal service voltage during normal system operation.

52 Pa.Code § 57.14 (b) and (c).

Mr. Rounce claimed that he has experienced a constant pattern of surges and spikes during his time as a PECO customer.  PECO’s equipment, the RVM, which was installed at the Service Address for ten days did not register any voltage variation beyond those allowed by 52 Pa.Code § 57.14.  According to PECO, the voltage variations that were recorded were the result of load coming into the Complainant’s service line due to his electric appliances.  Despite his distrust of PECO’s equipment and his own background in engineering, Mr. Rounce did not submit voltage measurements independent of PECO’s.  What Mr. Rounce did submit is a list of electrical appliances that he claimed were damaged by PECO’s service.  See Complainant Exhibit 5.  However, the damage claimed predates October 20, 2012, and it was unclear from Mr. Rounce’s testimony if any of it occurred during the brief period of time (September 30, 2012 to October 20, 2012) allowed by the statute of limitations in this matter.  66 Pa.C.S. § 3314(a).

With regard to the outages, it is an undisputed fact in this case that between January 1, 2011 and January 1, 2016, Mr. Rounce experienced 18 sustained power outages.  Of these 18 outages, two were related to public damage, two were potentially caused by lightning striking utility poles, two were caused by severe weather conditions, one resulted from an uprooted tree, and one was caused by a private contractor hitting PECO’s underground cable.  These eight outages resulted from events that PECO had no control over.

Of the remaining ten outages which occurred during the five-year period, two resulted from underground cable fault and eight from vegetation related issues.  PECO provided extensive testimony of the various programs that it has in place to address the underground cable fault events as well as the vegetation related outages.  The record in this matter shows that PECO has carefully tracked each instance of service interruption, has identified the circuit serving the Complainant as a problematic and a top priority circuit, and has progressively intensified its efforts to ensure service reliability.  This has been carried out in practice not only by conducting more aggressive tree trimming outside of the five-year cycle, but also by installing reclosers to isolate outages and by reconfiguring portions of the Middletown 352 circuit.  The result of PECO’s efforts is reflected in the decreasing number of service interruptions to one in 2011, two in 2012, and one in 2013.  The numbers of outages increased in 2014, but following the placement of Middleton 352 in PECO’s TPC for the year 2015, the number of outages decreased from nine in 2014 to five in 2015.  I note that of the five outages in 2015, only one – the underground cable fault on June 20, 2015 – resulted from conditions which were arguably within PECO’s control.

It is also important to note that PECO has already taken significant steps to provide Mr. Rounce the relief he requests.  The Company has reconfigured the Middletown 352 circuit so that a portion of the circuit is fed by another source.  It has already set in place recloser systems, whose purpose is to isolate sustained outages to the immediate areas and minimize the number of customers affected by the outage.  While it was Mr. Rounce’s intention to draw PECO’s attention to the quality of service that he is receiving, PECO provided credible evidence of being aware of the Middletown 352 circuit performance having made it a top priority circuit in 2011 and 2015 and including it in several reliability enhancement programs.

The Middletown 352 circuit crosses hilly terrain and heavily wooded areas characterized by tall, mature, trees with large canopies.  PECO’s witness testified credibly that the Company has complied with its vegetation management requirements.  While more can be done on the part of PECO to control the vegetation, I find that the Company has provided reasonable and adequate service to the Complainant by striving to address the problems and improve the service.  See Steve Atuahene v. PECO Energy Company, Docket No. C-2012-2299868, (Final Opinion and Order entered July 24, 2013).

As for the safety issue raised by Mr. Rounce, the record in this case does not support a finding that the work conducted by PECO on Wilton Woods Lane from August to November 2015, created an unsafe or hazardous condition for the residents in Mr. Rounce’s neighborhood.  PECO produced credible evidence that the work was necessary to restore service following an underground cable fault.  PECO’s witness testified that after investigating the underground cable responsible for the outage, PECO determined that 725 feet of it needed to be replaced.  This decision called for a PECO contractor to come to the scene and perform the replacement work.  Mr. Rounce did not elaborate why 81 days constituted an unreasonable amount of time to conduct the repairs in question, or why the conditions at the site were more unsafe than those one would expect at a site where similar work was being conducted.

For the reasons stated above, I conclude that the Complainant has failed to carry his burden of proving, by a preponderance of the evidence, that PECO has provided inadequate or unreasonable service to him.

CONCLUSIONS OF LAW

1.	The Commission has jurisdiction over the parties and the subject matter of this proceeding.  66 Pa.C.S.A. § 701.

2.	The Complainant seeking affirmative relief from the Commission has the burden of proving the Complaint allegations by producing evidence which established material facts by a preponderance of the evidence.  66 Pa.C.S.A. § 332(a).

3.	Every public utility shall furnish and maintain adequate, efficient, safe, and reasonable service and facilities, and shall make all such repairs, changes, alterations, substitutions, extensions, and improvements in or to such service and facilities as shall be necessary or proper for the accommodation, convenience, and safety of its patrons, employees and the public.  66 Pa. C.S.A § 1501.

4.	Service also shall be reasonably continuous and without unreasonable interruptions or delay.  66 Pa. C.S.A § 1501.

5.	A public utility is not obligated to provide perfect service and facilities 100% of the time.  A-Rize-N Management Co. LLC v. Pennsylvania American Water Co., Docket No. C-2009-2119162 (Order entered June 15, 2010).

6.	Tariffs filed with state regulatory agencies such as the public utility commission are not mere contracts but have the force of law and are binding on the consumer and the utility.  Stiteler v. Bell Telephone Company, 379 A.2d 339 (Pa.Cmwlth. 1977); Brockway Glass Company v. Pennsylvania Public Utility Commission, 437 A.2d 1067 (Pa.Cmwlth. 1981);

7.	For service rendered primarily for lighting purposes, the allowable variation in voltage measured at the service terminals of the customer may not exceed, for a longer period than 1 minute in each instance, 5% above or below the standard nominal service voltage and a total variation from minimum to maximum of 8% during normal system operation.  52 Pa.Code § 57.14 (b).

8.	For service rendered primarily for power purposes, the allowable variation in voltage measured at the service terminals of the customer may not exceed, for a longer period than 1 minute in each instance, 10% above or below the standard nominal service voltage during normal system operation.  52 Pa.Code § 57.14 (c).

9.	Mr. Rounce has failed to meet his burden of proving that he is entitled to the relief he is seeking from the Commission.

ORDER

THEREFORE,

IT IS ORDERED:

- That the formal Complaint filed by John J. Rounce against PECO Energy Company at Docket No. C-2015-2506941 is denied.

- That the Secretary’s Bureau should mark this matter closed.

Date:  August 4, 2016			/s/

Eranda Vero

Administrative Law Judge

For the purpose of PECO Exhibit 1, a storm event is defined as an outage affecting a certain number of customers on the PECO system.  Tr. 78, PECO Exhibit 1.  It does not relate to the weather conditions at the time of the outage.  Tr. 78.

Section 3314 of the Public Utility Code (the Code), provides a general limitation period of three years for any action under the Code, except as otherwise provided.  See 66 Pa.C.S. § 3314(a).  The present Complaint was filed on September 30, 2015.

Complainant Exhibit 1 lists eight sustained and momentary outages recorded by Mr. Rounce in 2010.  PECO did not submit information with regard to the number of sustained outages for the year 2010.  However, it is reasonable to conclude that they were numerous considering the fact that PECO classified the Middletown 352 circuit as a top priority circuit for the year 2011.

In reaching this conclusion, I do not consider the outage caused by an uprooted tree on July 11, 2015, to be an event within PECO’s control.

See Petition of PECO Energy Co. For Approval Of Its Long-Term Infrastructure Improvement Plan And To Establish A Distribution System Improvement Charge For Its Electric Operations, Docket No. P-2015-

2471423 (Order entered October 22, 2015) (“LTIIP Order”).