	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held June 14, 2017

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
	

	John F. Coleman, Jr.
	

	Robert F. Powelson

David W. Sweet
	

	
	

	Letter of Notification of PPL Electric Utilities Corporation, filed pursuant to 52 Pa. Code §57.72 57 Subchapter G for Approval to Rebuild Approximately 0.9 Miles of the Hosensack – Wescosville #3 230 kV Transmission Line in Lower Milford Township, Lehigh County, Pennsylvania 
	Docket Number:

A-2017-2601601


ORDER

BY THE COMMISSION:

On April 28, 2017, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code §57.72(d)(vi) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 
right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.

Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code §57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Lower Milford Township, Lehigh County Commissioners, and others.  No protests were filed.  No hearings were held.

PPL Electric requests approval to rebuild approximately 0.9 miles of the Hosensack – Wescosville #3 230 kV Transmission Line in Lower Milford Township, Lehigh County.  PPL Electric states that the 0.9-mile segment of existing transmission line has exceeded its useful life and must be rebuilt in order to continue to provide reliable service into the future.  PPL Electric also states that the rebuild is necessary to complete the communication path between the Hosensack 230-69 kV Substation and the Wescosville 500-230-138-69 kV Substation.  PPL Electric explains that in 2015, PPL Electric rebuilt approximately 8.9 miles of the 9.8 mile Hosensack-Wescosville #3 230 kV Transmission Line, which included the installation of fiber communication cable.
  PPL Electric proposes to rebuild the remaining 0.9 mile segment of the line to complete the communication link between the substations.  
PPL Electric notes that from the Hosensack 230-69 kV Substation, the Hosensack – Wescosville #3 Transmission Line extends approximately 0.9 miles to a tap point.  PPL Electric avers that it analyzed the existing lattice structures along this 0.9-mile segment of the line and found deterioration of the structural components, foundations, insulators, line hardware, shield wire, grounding, and signage.  PPL Electric also determined that the existing structures cannot accommodate the additional load of a fiber communication cable.  PPL Electric concludes that rebuilding the line would be the most prudent option, since the existing lattice structures are unable to accommodate the needed fiber communication cable.  PPL Electric explains further that the proposed rebuild will include an increase in vertical ground clearance, an increase in lightning protection, and installation of steel monopole structures for optimal structure longevity.  
The 0.9-mile segment of the line was constructed in the 1960s, and consists of three existing lattice tower structures and one 3-pole lattice angle structure.  Two of the existing structures will be replaced with new self-weathering steel monopole structures, and the other two existing structures will be replaced by new self-weathering steel 3-pole structures.  The new structures will be located generally within the same vicinity as the existing tower structures.  No new poles will be placed on any property that currently does not have an existing pole.  

The existing structures range in height from 88 to 120 feet.  The new monopoles will range between 150 and 165 feet in height, and the new 3-pole structures will range from 77 to 115 feet in height.  All new poles will be self-supported, either direct embedded or on concrete caisson foundations.  

The project will be built within the existing right-of-way (ROW) for the Hosensack-Wescosville #3 230 kV Transmission Line, and on property owned in fee by PPL Electric.   The ROW is 450 feet in width.  PPL Electric provides that it has designed the rebuilt segment of the Hosensack-Wescosville #3 230 kV Transmission Line to fit within the existing ROW.  No additional ROW is needed.  

PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  

PPL Electric states that the total estimated cost for the proposed project is approximately $500,000, and will be paid for, owned and operated by PPL Electric.  Construction of the project is proposed to commence in September 2017 with a proposed in-service date of November 2017.    
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(vi) because the proposed 0.9-mile segment of rebuilt Hosensack – Wescosville #3 230 kV Transmission Line is less than 2.0 miles in length.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,
IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric Utilities Corporation, for approval to rebuild approximately 0.9 miles of the Hosensack – Wescosville #3 230 kV Transmission Line in Lower Milford Township, Lehigh County, Pennsylvania,  is hereby approved.  
2. That this proceeding at Docket No. A-2017-2601601 be closed. 
BY THE COMMISSION,

[image: image1.png]



Rosemary Chiavetta
Secretary

ORDER ADOPTED: June 14, 2017
ORDER ENTERED:  June 14, 2017
� See Letter of Notification of PPL Electric Utilities Corporation for Approval of the Reconstruction of the Hosensack-Wescosville 230 kV Transmission Line in Upper Macungie, Lower Macungie, Upper Milford and Lower Milford Townships, Lehigh County, Pennsylvania, Docket No. A-2011-2237599 (Order entered August 25, 2011). 





5

