	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held July 12, 2017

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
	

	John F. Coleman, Jr.
	

	Robert F. Powelson

David W. Sweet
	

	
	

	Letter of Notification of PPL Electric Utilities Corporation, filed pursuant to 52 Pa. Code §57.72 57 Subchapter G for Approval to Re-Terminate and Reconductor Approximately 0.3 Miles of 230 kV Transmission Line in Milton Borough, Northumberland County, Pennsylvania 
	Docket Number:

A-2017-2605101


ORDER

BY THE COMMISSION:

On May 17, 2017, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code §57.72(d)(vi) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 
right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.

Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code §57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Milton Borough, Northumberland County Commissioners, and others.  No protests were filed.  No hearings were held.

The Milton 230-69 kV Substation is currently connected to the Montour – Sunbury 230 kV transmission Line.  This 22.9 mile long transmission line also connects to the Sunbury and Montour Substations.  PPL Electric’s standard design for all 230 kV transmission lines is to terminate into only two substations, with one substation at either end.  PPL Electric explains that this standard enhances system reliability by simplifying interconnections and makes it easier for PPL Electric to isolate system faults.  The Montour – Sunbury 230 kV Transmission line in its present configuration does not comply with the PPL Electric design standard for 230 kV lines, since it is connected to three substations.  

The Milton Substation was built in 1973 and serves approximately 13,000 customers.  The Milton Substation is connected directly to the Montour – Sunbury 230 kV Transmission Line with no interrupting device for the 230-69 kV transformer at the Milton Substation.  PPL Electric’s design standard is to connect a transformer to a transmission line through an interrupting device, such as a circuit breaker.  PPL Electric notes that this prevents a transformer failure from interrupting service along the entire transmission line and prevents a line outage from interrupting the transformer.   

PPL Electric proposes to remove the current 300 foot tap from the Montour-Sunbury Transmission Line to the Milton Substation.  PPL Electric provides that the Montour-Sunbury Transmission Line will be split near the Milton Substation into the Milton-Montour Transmission Line and the Milton-Sunbury Transmission Line.  The existing 300 foot tap will be replaced with two new 300 foot taps to re-terminate the two new sections of 230 kV line into the Milton Substation.  PPL Electric also proposes to reconductor each transmission line for approximately 450 feet (the first span) of each 230 kV line to facilitate the new taps.  In total, PPL Electric proposes to construct approximately 600 feet of new transmission line and reconductor approximately 900 feet of transmission line within the existing right-of-way (total of approximately 0.3 miles).  
PPL Electric submitted the proposed project to PJM Interconnection, LLC (PJM) for review and inclusion in the PJM Regional Transmission Expansion Plan.  The project was presented before the Transmission Expansion Advisory Committee and approved by the PJM Board as supplemental project s0857.  
PPL Electric states that it will remove one existing steel pole structure and install two new steel monopole dead-end structures.  The existing steel pole being removed has a height of 125 feet.  The two new steel monopole dead-end structures will be installed on concrete caisson foundations and will have an average height of approximately 115 feet.  

PPL Electric explains that the proposed work will be located on property owned in fee by PPL Electric for the Milton 230-69 kV Substation (80%) and within the existing right-of-way for the Montour-Sunbury 230 kV Transmission Line (20%).  No additional rights-of-way are required for the project.

PPL Electric states that the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  

PPL Electric states that the total estimated cost for the proposed project is approximately $2.2 million, and will be paid for, owned and operated by PPL Electric.  Construction of the project is proposed to commence in September 2017 with a proposed in-service date of December 2017.    
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(vi) because the two new 230 kV tap lines and reconductored segments of the new Milton-Montour and Milton-Sunbury 230 kV Transmission Lines will total less than two miles, .i.e., approximately 0.3 miles.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,
IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric Utilities Corporation, for approval to re-terminate and reconductor approximately 0.3 miles of 230 kV Transmission Line in Milton Borough, Northumberland County, Pennsylvania,  is hereby approved.  
2. That this proceeding at Docket No. A-2017-2605101 be closed. 
[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

ORDER ADOPTED: July 12, 2017
ORDER ENTERED: July 13, 2017
5

