	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held August 31, 2017

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
	

	David W. Sweet
	

	John F. Coleman, Jr.
	

	
	

	Letter of Notification of PPL Electric Utilities, 
for Approval to Rebuild Approximately 8.5 Miles of Existing 138/69 kV Transmission Lines in Franconia and Hatfield Townships, Montgomery County and West Rockhill Township, Bucks County, Pennsylvania 
	Docket Number:

A-2017-2613595


ORDER

BY THE COMMISSION:

On July 7, 2017, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code § 57.72(d)(1)(i) and (v) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 

right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.


Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code § 57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Franconia Township, Montgomery County Commissioners, et al.  No protests were filed.  No hearings were held.
PPL Electric requests approval to rebuild approximately 8.5 miles of 138/69 kV transmission lines located in Franconia and Hatfield Townships, Montgomery County and West Rockhill Township, Bucks County, Pennsylvania.  PPL Electric states that the transmission lines to be rebuilt consist of the approximately 7.8-mile Buxmont-Elroy #1 and #2 69 kV transmission lines, the approximately 0.25-mile Elroy-Hatfield #1 and #2 138/69 kV transmission lines, the approximately 0.35-mile Elroy #1 and #2 138/69 kV transmission taps, and the approximately 354-foot Hatfield #1 and #2 69 kV transmission taps.  
The existing Buxmont-Elroy #1 and #2 69 kV transmission lines extend approximately 7.8 miles between the Buxmont Substation located in West Rockhill Township, Bucks County, and the tap point with the Elroy Substation located in Hatfield Township, Montgomery County.  The double-circuit Buxmont-Elroy #1 and #2 69 kV transmission lines were constructed in the early 1950s.  

The Elroy #1 and #2 138/69 kV transmission taps interconnect the Buxmont-Elroy #1 and #2 138/69 kV lines with the Elroy Substation.  These taps extend approximately 
0.35 miles from the transmission line right-of-way (ROW) to the Elroy Substation.  The taps were constructed in the late 1960s.
The existing Elroy-Hatfield #1 and #2 138/69 kV transmission lines extend approximately 0.25 miles from the tap point with Elroy Substation to the Hatfield Substation located in Hatfield Township.  The double-circuit Elroy-Hatfield #1 and #2 138/69 kV transmission lines were constructed in the late 1960s.

The Hatfield #1 and #2 69 kV transmission taps interconnect the Elroy-Hatfield #1 and #2 138/69 kV transmission lines and Hatfield Substation and are located in Hatfield and Franconia Townships, Montgomery County.  These transmission taps were constructed in the late 1960s.

PPL Electric states that it has evaluated these transmission lines and concluded that the lines have reached the end of their useful life and must be replaced to ensure continued safe and reliable electric service.  PPL Electric uses an Asset Optimization Strategy to systematically identify and modernize its aging facilities.  The measures used to identify equipment and lines that qualify for this work include age, condition, criticality of the equipment or line, and circuit performance.  PPL Electric analyzed these transmission lines and found deterioration of the structural components, foundations, hardware, and signage.  PPL Electric evaluated the cost to rehabilitate the lines and taps and concluded that the total cost to rehabilitate these lines would be greater than the cost to completely rebuild them within the same ROW.  Additionally, the existing conductors and structures do not meet current design or height standards.  
PPL avers that the project, which is the subject of this LON, will bring the Buxmont-Elroy #1 and #2 69 kV transmission lines, the Elroy-Hatfield #1 and #2 138/69 kV transmission lines, the Elroy #1 and #2 138/69 kV transmission taps, and the Hatfield #1 and #2 69 kV transmission taps into compliance with current design standards, including increased vertical ground clearance and steel monopoles for optimal structure longevity.  PPL Electric further states that each of the lines will be rebuilt for future double-circuit 
138 kV operation, but will initially be operated as double-circuit 69 kV lines.
PPL Electric states that it will remove 208 existing wood poles and 1 steel pole and install 174 new steel monopole structures.  The existing structures range in height from 60 to 105 feet.  The new monopole structures will be self-supported, either directly embedded or on concrete caisson foundations and will be approximately 5 to 30 feet taller than the existing structures.
In its filing, PPL Electric states that the proposed project has been designed and will be built entirely within the existing ROW of the Buxmont-Elroy #1 and #2 69 kV transmission lines, the Elroy-Hatfield #1 and #2 138/69 kV transmission lines, the Elroy #1 and #2 138/69 kV transmission taps, and the Hatfield #1 and #2 69 kV transmission taps.  PPL further states that the existing ROW generally varies from 40 to 100 feet in width.  No additional ROW is needed.
PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  

PPL Electric states that the total estimated cost for the proposed project is approximately $13.3 million, and will be owned, operated, and paid for by PPL Electric.  Construction of the project is proposed to commence in September 2017 with a proposed 
in-service date of June 2018.
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(i) and (v) because the proposed project reconstructs the Buxmont-Elroy #1 and #2 69 kV transmission lines, the Elroy-Hatfield #1 and #2 138/69 kV transmission lines, the Elroy #1 and #2 138/69 kV transmission taps, and the Hatfield #1 and #2 69 kV transmission taps in such a manner that the ROW is not substantially altered.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  

We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,
IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric, for approval to rebuild approximately 8.5 miles of existing 138/69 kV transmission line in Franconia and Hatfield, Montgomery County and West Rockhill Township, Bucks County, Pennsylvania, is hereby approved.  
2. That this proceeding at Docket No. A-2017-2613595 be closed. 
[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

ORDER ADOPTED: August 31, 2017
ORDER ENTERED:  August 31, 2017
6

