	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held September 21, 2017

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
	

	David W. Sweet
	

	John F. Coleman, Jr.
	

	
	

	Letter of Notification of PPL Electric Utilities, for Approval to Rebuild Approximately 
9.8 Miles of the Siegfried-Jackson #1 and #2 
138 kV Transmission Line in Chestnuthill, Jackson and Polk Townships, Monroe County, Pennsylvania 
	Docket Number:

A-2017-2617261


ORDER

BY THE COMMISSION:

On August 1, 2017, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code § 57.72(d)(1)(v) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 

right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.


Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code § 57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Monroe County Commissioners, Chestnuthill, Polk, and Jackson Townships, et al.  No protests were filed.  No hearings were held.
PPL Electric requests approval to rebuild approximately 9.8 miles of the double-circuit Siegfried-Jackson #1 and #2 138 kV Transmission Line (Siegfried-Jackson) located in Chestnuthill, Jackson and Polk Townships, Monroe County, Pennsylvania.  The section of the Siegfried-Jackson transmission line to be replaced extends from the Jackson 

138-69 kV Substation (Jackson Substation) to a structure just south of the Gilbert 138-12 kV Substation (Gilbert Substation) located in Polk Township.  PPL Electric states that this section of the Siegfried-Jackson is referred to as the Jackson-Gilbert transmission line.  The existing conductors will be transferred to the new transmission structures.
The Jackson-Gilbert transmission line primarily consists of 96 wood poles constructed around 1974 and 56 steel structures.  PPL Electric states that it will remove 96 existing wood poles and six steel poles and install 102 new steel monopole structures.  The existing structures range in height from 45 to 105 feet.  The new monopole structures will be self-supported, either directly embedded or on concrete caisson foundations and will range in height from 45 to 110 feet with most structures being approximately 95 feet in height.  One additional steel monopole will be installed on PPL Electric land owned in fee.
PPL Electric states that it has evaluated the transmission line facilities and concluded that they must be replaced to ensure continued safe and reliable electric service.  PPL Electric uses an Asset Optimization Strategy to systematically identify and modernize its aging facilities.  The measures used to identify equipment and lines that qualify for this work include age, condition, criticality of the equipment or line, and circuit performance.    PPL Electric avers that the Siegfried-Jackson transmission line, including the section to be replaced, is ranked amongst its worst performing circuits.  
PPL Electric has concluded that the wood poles, described above, have reached the end of their reliable service life.  PPL Electric further states that the cellon material used for treatment of the wood poles was, at the time, believed to be an economic technology with a similar life expectancy as alternative treatments.  However, this material is no longer used because wood pole manufacturers determined that these cellon treated poles become susceptible to advanced aging and internal wood rot leading to pole failure.  The resulting short service life led wood pole manufacturers to discontinue cellon treated wood poles and to recommend the replacement of all cellon treated wood poles at or near the end of their service life.  

PPL Electric states that in addition to replacement of the wood poles, six of the steel structures must be replaced to avoid engineering issues such as the need to install additional mid-span poles due to differences in structure height.  PPL Electric further states that the additional structure is needed due to increased structural loading from new optical ground wires which it plans to install as part of the rebuild.
PPL Electric avers that the Jackson-Gilbert rebuild will also bring it into compliance with current design standards, including increased vertical ground clearance and steel monopoles for optimal structure longevity.  PPL Electric further states that the rebuild will include new optical ground wires to increase the lightning protection of the transmission line and provide a communication path between the Jackson Substation and Gilbert Substation.
In its filing, PPL Electric states that the proposed project has been designed and will be built entirely within the existing right-of-way (ROW) of the Siegfried-Jackson transmission line.  PPL Electric further states that the existing ROW generally varies from 
50 to 125 feet in width.  No additional ROW is needed.

PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  

PPL Electric states that the total estimated cost for the proposed project is approximately $9.1 million, and will be paid for by PPL Electric.  Construction of the project is proposed to commence in October 2017 with a proposed in-service date of 
May 2018.
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(v) because the proposed project reconstructs approximately 9.8 miles of the double-circuit Siegfried-Jackson #1 and #2     138 kV Transmission Line in such a manner that the ROW is not substantially altered.   Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  

We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,
IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric, for approval to rebuild approximately 9.8 miles of the Siegfried-Jackson #1 and #2 138 kV Transmission Line in Chestnuthill, Jackson and Polk Townships, Monroe County, Pennsylvania, is hereby approved.  

2. That this proceeding at Docket No. A-2017-2617261 be closed. 
[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta
Secretary

ORDER ADOPTED: September 21, 2017
ORDER ENTERED: September 21, 2017
3

