	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held March 15, 2018

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
Norman J. Kennard
	

	David W. Sweet
	

	John F. Coleman, Jr.
	

	
	

	Letter of Notification of PPL Electric Utilities, for Approval to Rebuild the Approximately 
3.2-Mile Bartonsville 138 kV Transmission Tap in Pocono and Stroud Townships, Monroe County, Pennsylvania 
	Docket Number:

A-2018-2643411


ORDER

BY THE COMMISSION:

On January 16, 2018, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code § 57.72(d)(1)(i) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 

right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.


Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code § 57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Monroe County Commissioners, Pocono and Stroud Townships, et al.  No protests were filed.  No hearings were held.
PPL Electric requests approval to rebuild the approximately 3.2-mile Bartonsville 138 kV Transmission Tap (Bartonsville Tap) located in Pocono and Stroud Townships, Monroe County, Pennsylvania.  The Bartonsville Tap extends from the Monroe-Jackson #1 and #2 138 kV Transmission Line (Monroe-Jackson) in Pocono Township to the Bartonsville 138-12 kV Substation (Bartonsville Substation) located in Stroud Township.  The Bartonsville-Tap is single-circuit with the exception of a portion, approximately 0.1 miles in length, consisting of the first two spans from the Monroe-Jackson transmission line which is double circuit. 
PPL Electric states that the proposed project (Project) includes the replacement of all existing conductors and wood transmission structures on the Bartonsville Tap.  PPL Electric further states that the Project also rebuilds the entire Bartonsville Tap as a double-circuit tap and includes the installation of new optical ground wires.
The Bartonsville Tap primarily consists of 58 wood poles constructed around 1986 and 4 steel structures.  The steel structures were installed in 2009 and will not be replaced as part of the Project.  PPL Electric states that it will remove the 58 existing wood poles and install 51 new steel monopole structures.  The existing structures range in height from 61 to 84 feet.  The new monopole structures will be self-supported, either directly embedded or on concrete caisson foundations and will range in height from 79 to 106 feet with an average height of approximately 87 feet.
PPL Electric states that it has evaluated the transmission line facilities and concluded that they must be replaced to ensure continued safe and reliable electric service.  PPL Electric uses an Asset Optimization Strategy to systematically identify and modernize its aging facilities.  The measures used to identify equipment and lines that qualify for this work include age, condition, criticality of the equipment or line, and circuit performance.  PPL Electric further states that the Project was presented at the PJM Mid-Atlantic 
Sub-Regional Transmission Expansion Planning stakeholder meeting and assigned supplemental project number s1031.  
PPL Electric has concluded that the conductors, hardware and wood poles, described above, have reached the end of their reliable service life.  PPL Electric further states that the cellon material used for treatment of the wood poles was, at the time, believed to be an economic technology with a similar life expectancy as alternative treatments.  However, this material is no longer used because wood pole manufacturers determined that these cellon treated poles become susceptible to advanced aging and internal wood rot leading to pole failure.  The resulting short service life led wood pole manufacturers to discontinue cellon treated wood poles and to recommend the replacement of all cellon treated wood poles at or near the end of their service life.  

PPL Electric avers the modernization of the line will help ensure reliable and continuous service to customers in Monroe County.  The Bartonsville Tap rebuild will improve service reliability and bring the transmission tap into compliance with current design and lightning protection standards.  PPL Electric states that the double-circuit design will provide increased transfer capability, improve operational flexibility and allow the Bartonsville Substation to be converted to a more reliable configuration.  The Project will also provide increased vertical ground clearance, steel monopoles for optimal structure longevity, and optical ground wires to increase the lightning protection of the transmission line.  
In its filing, PPL Electric states that the proposed project has been designed and will be built entirely within the existing right-of-way (ROW) of the Bartonsville Tap.  PPL Electric further states that the existing ROW is 100 feet in width and that no additional ROW is needed.
PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  

PPL Electric states that the total estimated cost for the proposed project is approximately $8.9 million and will be paid for by PPL Electric.  Construction of the project is proposed to commence in April 2018 with a proposed in-service date of 
May 2019.
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(i) because the proposed project reconstructs approximately 3.2 miles of the Bartonsville 138 kV Transmission Tap in such a manner that the ROW is not substantially altered.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric, for approval to rebuild the 3.2-mile Bartonsville 138 kV Transmission Tap in Pocono and Stroud Townships, Monroe County, Pennsylvania, is hereby approved.  

2. That this proceeding at Docket No. A-2018-2643411 be closed. 

[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta

Secretary

ORDER ADOPTED: March 15, 2018
ORDER ENTERED:  March 15, 2018
5

