	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held June 14, 2018

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
Norman J. Kennard
	

	David W. Sweet
	

	John F. Coleman, Jr.
	

	
	

	Letter of Notification of PPL Electric Utilities Corporation, for Approval to Rebuild Approximately 6.4 Miles of Existing 138 kV Transmission Line in Polk and Eldred Townships, Monroe County, Pennsylvania 
	Docket Number:

A-2018-3001324


ORDER

BY THE COMMISSION:

On April 19, 2018, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code § 57.72(d)(1)(i) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 

right-of-way.
(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing
transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.
   (vi) An HV line having a proposed route of 2 miles or less.


Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code § 57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Monroe County Commissioners, Polk and Eldred Townships, et al.  No protests were filed.  No hearings were held.
PPL Electric requests approval to rebuild approximately 6.4 miles of 138 kV transmission line in Polk and Eldred Townships, Monroe County, Pennsylvania.  The subject section of double-circuit transmission line is part of the Siegfried-Jackson #1 & #2 138 kV Transmission Line (Siegfried Jackson) and located between a transmission line structure just south of PPL Electric’s Gilbert 138-12 kV Substation (Gilbert Substation) located in Polk Township, Monroe County and a structure located at the junction with the de-energized Little Gap 69 kV Transmission Tap in Eldred Township, Monroe County.  This section of transmission line will be referred to as the Gilbert-Little Gap Tap.
PPL Electric states that rebuilding the Gilbert-Little Gap Tap is necessary to enable PPL Electric to continue to provide reliable service now and into the future and that the Siegfried-Jackson, including the Gilbert-Little Gap Tap, is ranked in the top 5% of its worst performing circuits.  A combination of lightning strikes and failed insulators, switches, and structures have contributed to over 50 outages on the Siegfried-Jackson in the previous ten years.  PPL Electric further states that 37 outages are attributed to lightning, six of the outages are attributed to failed insulators and switches, and one outage is attributed to a structure failure.  The remainder of the outages are from unknown causes.  PPL Electric avers that these outages affect over 17,000 customers.
PPL submits that the Gilbert-Little Gap Tap rebuild will ensure continued reliable service by bringing the transmission line into compliance with current design standards and providing increased lightning protection to reduce the frequency of momentary outages.  PPL Electric further states that the rebuild will allow for sectionalizing of the transmission system to restore service to customers in instances of sustained outages or maintenance scenarios.  
PPL Electric uses an Asset Optimization Strategy to systematically identify and modernize its aging facilities.  The measures used to identify equipment and lines that qualify for this work include age, condition, criticality of the equipment or line, and circuit performance.
PPL Electric states that the proposed project (Project) includes the replacement of all wood transmission structures on the Gilbert-Little Gap Tap and eight steel structures.  The project also includes the installation of a dual optical ground wire and load break air break switches.  PPL Electric further states that the existing conductors will be reused except in sections where it is deemed more cost effective to replace both the conductors and transmission structures.  There will be no change to the line’s voltage, which will continue at 138 kV.
The Gilbert-Little Gap Tap contains 70 wood poles constructed around 1974 and 13 steel structures.  PPL Electric states that it will remove the existing wood poles and eight of the steel poles and install 55 new steel monopole structures and 23 new steel two-pole structures.  The existing structures range in height from 45 to 105 feet with an average height of about 85 feet.  The new steel structures will average approximately 95 feet in height.
PPL Electric has concluded that 61 of the wood poles, described above, have reached the end of their reliable service life.  PPL Electric further states that the cellon material used for treatment of these wood poles was, at the time, believed to be an economic technology with a similar life expectancy as alternative treatments.  However, this material is no longer used because wood pole manufacturers determined that these cellon treated poles become susceptible to advanced aging and internal wood rot leading to pole failure.  The resulting short service life, approximately 35 years, led wood pole manufacturers to discontinue cellon treated wood poles and to recommend the replacement of all cellon treated wood poles at or near the end of their service life.  
PPL Electric states that the remaining nine wood poles are being replaced because they failed the engineering loading analysis for the addition of the dual overhead optical ground wire on the line.  PPL Electric further states that because of the additional weight reuse of these poles would require additional mid-span structures where no structures currently exist.
In its filing, PPL Electric states that the proposed project has been designed and will be built entirely within the existing right-of-way (ROW) of the Gilbert-Little Gap Tap.  PPL Electric further states that the existing ROW generally varies from 50 to 100 feet in width and that no additional ROW is needed.
PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  

PPL Electric states that the total estimated cost for the proposed project is approximately $5.9 million and will be paid for by PPL Electric.  Construction of the project is anticipated to commence in July 2018 with a proposed in-service date of July 2019.
The formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(i) because the proposed project reconstructs approximately 6.4 miles of 138 kV transmission line in such a manner that the ROW is not substantially altered.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  
We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by PPL Electric Utilities Corporation, for approval to rebuild 6.4 miles of 138 kV transmission line in Polk and Eldred Townships, Monroe County, Pennsylvania, is hereby approved.  
2. That upon completion of the subject project, PPL Electric Utilities Corporation shall file the final project cost with the Commission.

3. That upon completion of ordering paragraph 2, this proceeding at Docket 
No. A-2018-3001324 be closed. 

BY THE COMMISSION,

[image: image1.png]



Rosemary Chiavetta

Secretary

ORDER ADOPTED: June 14, 2018
ORDER ENTERED: June 14, 2018
5

