	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held July 12, 2018

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman

Norman J. Kennard, dissenting
	

	David W. Sweet
	

	John F. Coleman, Jr., Statement, concurring in result only
	

	
	

	Letter of Notification of PPL Electric Utilities, 

for Approval to Rebuild the Existing Breinigsville-Alburtis 500 kV Transmission Line in Lower Macungie and Upper Macungie Townships, Lehigh County, Pennsylvania 
	Docket Number:

A-2017-2635709


ORDER

BY THE COMMISSION:

On November 27, 2017, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code §57.72(d)(1)(i) of the Commission’s transmission line siting regulation.  Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 

right-of-way.

(ii) An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing

transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

   (vi) An HV line having a proposed route of 2 miles or less.


Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code §57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Lower Macungie and Upper Macungie Townships, Lehigh County Commissioners, et al.  No protests were filed.  No hearings were held.

PPL Electric proposes to rebuild the existing Breinigsville-Alburtis 500 kV Transmission Line (Breinigsville-Alburtis) in Lower Macungie and Upper Macungie Townships, Lehigh County, Pennsylvania.  The Breinigsville-Alburtis is a six-mile-long single-circuit transmission line that extends from the Breinigsville 500-138-69 kV Substation (Breinigsville Substation) in Upper Macungie Township to the Alburtis 

500-230 kV Substation (Alburtis Substation) in Lower Macungie Township.

PPL Electric states that the proposed project (Proposed Project) consists of rebuilding the line as a double-circuit transmission line and includes the replacement of all existing transmission line structures and the installation of two new structures.  The transmission line will be renamed the Breinigsville-Alburtis #1 & #2 500 kV Transmission Line (Breinigsville-Alburtis #1 & #2).


PPL Electric avers that the Proposed Project is part of a larger project which includes the reconfiguration of the Wescosville 500-138-69 kV Substation (Wescosville Substation) switchyard and involves re-termination of the existing Breinigsville-Alburtis.
  PPL Electric states that the second circuit and switch yard reconfiguration will enable it to resolve an existing North American Electric Reliability Corporation (NERC) standard violation regarding voltage drop on the 138 kV and 69 kV systems during a contingency event.  PPL Electric further states that the Proposed Project will also enable it to bring its Wescosville Substation up to current design standards.

PPL Electric states that the Proposed Project is necessary to resolve a NERC standard violation.  PPL Electric further states that the Proposed Project will improve the reliability of the Breinigsville Substation by providing a third 500 kV source.  Currently the Breinigsville Substation only has two sources, the Wescosville-Breinigsville 500 kV Transmission Line and the Breinigsville-Alburtis line.  PPL Electric avers that during maintenance scenarios when one of the two 500 kV transmission lines is taken out-of-service and a fault occurs on the other transmission line in-service, the entire Breinigsville Substation loses power.  PPL Electric states that the addition of a third 500 kV source will avoid interruptions during maintenance of these 500 kV lines and for certain contingency events.

  The addition of the second 500 kV circuit to the existing Breinigsville-Alburtis transmission line was presented at the PJM Mid-Atlantic Sub-Regional Transmission Expansion Plan committee and approved as supplemental project number S0864. 

The existing transmission structures cannot support the double-circuit configuration and will be replaced as part of the Proposed Project.  PPL Electric states that the Proposed Project includes the replacement of 27 existing transmission structures and the construction of two new structures.  The new structures will range from approximately 115 to 195 feet in height and that the existing structures to be replaced range from 115 to 185 feet in height.  PPL Electric further states that the Proposed Project has been designed and will be built entirely within the existing ROW for the Breinigsville-Alburtis transmission line and on PPL Electric’s property for the Breinigsville Substation and Alburtis Substation.  The existing ROW is approximately 200 feet in width.  No additional ROW is needed.
PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.

PPL Electric states that the total estimated cost for the proposed project is approximately $33 million, and will be owned, operated and paid for by PPL Electric.  Construction of the project is proposed to commence in May 2018 with a proposed in-service date of March 2019.


The Commission initiated four sets of data requests regarding this LON.  PPL Electric responded in January, April, and July of 2018, and submitted the following information:

· The Breinigsville-Alburtis 500 kV Transmission Line is about 37 years old with a useful life expectancy of approximately 80 years.

· There have been no unplanned outages for either the Wescosville-Breinigsville     500 kV Transmission Line or the Breinigsville-Alburtis line over the past three years.

· Approximately 95 MW consisting of 10,000 customers would have to be dropped prior to the second contingency occurring to prevent the violation.  The Company later confirmed, upon further data requests, that if the N-1-1 condition were to occur prior to completion of the subject project, PPL Electric would utilize operational steps to prevent the low voltage and voltage drop violation.  These operational steps are an interim solution until the subject project is complete.  Per the Company, a protection control system is a “Special Protection Scheme (SPS)” or “Remedial Action Scheme (RAS)”.  PJM Manual 7 states “SPS/RAS’s should not be installed as a substitute for good system design or operating practices.  Their implementation is generally limited to temporary conditions involving the outage of critical equipment.”  PPL Electric would only utilize an SPS/RAS on a temporary basis and not as a permanent substitute for proper system design.

· The Breinigsville substation primarily feeds industrial load customers on the transmission and distribution systems but there are also residential customers sourced from this substation.  There are no critical customers among the 10,000 that would be dropped.

· PPL Electric did not provide any information on the probability of such an N-1-1 condition.This project is not a regional reliability project, but a supplemental transmission project filed by PPL Electric for the sole purpose of alleged reliability benefits to its distribution system customers.


Under the Commission’s siting regulations at 52 Pa. Code § 57.71 et seq., the Company must establish a clear need for the Project.
  PPL Electric has not adequately proven the need for this project.  Specifically, the Company has not established a reasonable likelihood that the alleged events leading to an outage event are likely to occur, nor has it demonstrated that the proposed solution is an efficient and cost-effective choice relative to other alternatives.


The Company avers that service would be lost if only one of the lines associated with the N-1-1 condition occurs.  However, it would appear that an SPS or RAS could be effectuated that would maintain service if only one line went down.  PPL Electric avers that this is not its preferred final solution, but an “interim” solution.  However, whether or not the Company has preferred solutions to an alleged reliability problem is not dispositive of the establishment of the need for the project.  As to reliability, PPL Electric has not clearly established a reasonable likelihood of both lines having an outage in the same time frame.  In fact, the data request responses in this case have not identified any unplanned outages associated with both lines.  Moreover, the lines are not aged facilities requiring replacement.


In the event that a severe event occurred, the loss of a tower on the new double-circuit transmission would not avoid the outage.  Moreover, if a severe weather event did cause the loss of both lines, the damage to the distribution system would likely be equally, if not more severe, such that load would likely be significantly reduced, obviating the need to prevent the voltage drop on the 138 kV and 69 kV systems.  It is not clear that load would need to be dropped under such an event.  Based on the information provided by PPL Electric in its original filing and answers to Commission staff data requests, we do not believe that PPL Electric has met its burden under 52 Pa. Code § 57.72(c)(5) to demonstrate the need for the subject project.


It should be noted that we do not take this action lightly.  However, this filing presents some rather unique characteristics, including replacement of a well-functioning facility well before its full life expectancy, failure to fully resolve a potential threat that PPL Electric alleges to fix, failure to reasonably quantify the alleged reliability benefits of the project, and failure to fully assess alternative solutions to the alleged reliability issues.  Given these shortcomings, we have concluded that this project clearly distinguishes itself from previous projects that we have approved in the past.


This Commission has a responsibility to ensure that substantial investments are prudently made, particularly those filed as supplemental projects.  Because this is a supplemental project, no other third party like PJM has performed a cost benefit analysis or assessed alternatives.
  Moreover, PPL Electric has filed a vastly disproportionate number of such supplemental projects.  As of August 30, 2017, the Company was responsible for 

$2.9 Billion of the $3.1 Billion to be spent on supplemental projects in Pennsylvania, 

or 93% of such spending.  According to our annual Rate Comparison Report, PPL Electric’s transmission rates have increased 175% since January 31, 2006, with almost all of that increase starting in 2013.  Between 2013 and 2018, PPL Electric’s transmission rates increased 19% each year.  While this history and inventory of past and future transmission project costs do not have a direct relevance to the particular circumstances to this proposed project, they do highlight the need for further scrutiny by all interested parties to ensure the requirements of 52 Pa. Code § 57.72(5) and 52 Pa. Code § 57.76(a)(4) are met, particularly for supplemental projects, and that electric distribution companies in Pennsylvania are expected to provide more information to justify these expenditures going forward.



Given PPL Electric’s failure to demonstrate the need for the proposed project and examine available alternatives, we must deny PPL Electric’s LON and direct PPL Electric to comply with the application process set forth in 52 Pa. Code § 57.72.  To the extent the Company modifies its LON or files an application and thus provides evidence that this project is an optimal means to enhance reliability on its transmission and distribution systems in a cost-effective manner, we are always open to reconsideration.  However, at the current time, PPL Electric has not carried its burden to prove the need for this project and examine available alternatives.  THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by the PPL Electric Utilities Corporation, for approval to rebuild the existing Breinigsville-Alburtis 500 kV Transmission Line in Lower Macungie and Upper Macungie Townships, Lehigh County, Pennsylvania, is hereby denied.  

2. That PPL Electric Utilities Corporation comply with the application process set forth in 52 Pa. Code § 57.72 as required by 52 Pa. Code § 57.72(d)(5).
3. That upon completion of Ordering Paragraph 2, this proceeding at Docket 

No. A-2017-2635709 be closed. 
[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta

Secretary

ORDER ADOPTED: July 12, 2018

ORDER ENTERED: August 3, 2018
� A-2017-2618099, Letter of Notification of PPL Electric Utilities Corporation, for Approval to Replace and Re-terminate Approximately 200 feet of the Existing Breinigsville-Alburtis 500 kV Transmission Line in Lower Macungie Township, Lehigh County, Pennsylvania, Order entered August 31, 2017.


� 52 Pa. Code § 57.72(5) states that an application shall contain a general statement of need for the proposed HV line in meeting identified present and future demands for service, of how the proposed HV line will meet that need and of the engineering justifications for the proposed HV line.


� 52 Pa. Code § 57.76(a)(4) requires that the Commission finds and determines that a proposed HV line… will have minimum adverse environmental impact, considering the electric power needs of the public, the state of available technology and the available alternatives.


� PJM simply notes supplemental projects for purposes of outage planning.





5

