	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA.  17105-3265
	


	
	Public Meeting held September 20, 2018

	Commissioners Present:
	


	Gladys M. Brown, Chairman
	

	Andrew G. Place, Vice Chairman
Norman J. Kennard, Joint Statement, dissenting
	

	David W. Sweet
	

	John F. Coleman, Jr., Joint Statement, dissenting
	

	
	

	Petition for Waiver of Certain Provisions of the Commission’s Regulations for Commission Review of Siting and Construction of Electric Transmission Lines set forth at 52 Pa. Code § 57.71 et seq.
Letter of Notification of PPL Electric Utilities Corporation, for Approval to Rebuild Approximately 6.9 Miles of Existing 138/69 kV Transmission Line in Washington Township, Lehigh County and the Borough of Palmerton and Lower Towamensing and East Penn Townships, Carbon County, Pennsylvania 

	Docket Number:

A-2018-3001477


ORDER

BY THE COMMISSION:

On April 20, 2018, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Petition seeking a waiver in order to file a Letter of Notification (LON) under 52 Pa. Code § 57.72(d) in lieu of an application under 52 Pa. Code §§ 57.71 and 57.72(a)-(c).  PPL Electric also filed an LON pursuant to 52 Pa. Code § 57.72(d) of the Commission’s transmission line siting regulation.
Petition for Waiver

PPL Electric filed a Petition for Waiver of certain provisions of the Commission’s regulations for Commission Review of Siting and Construction of Electric Transmission Lines set forth at 52 Pa. Code 57.71 et seq.  Specifically, PPL Electric seeks a waiver of 52 Pa. Code § 57.72(d) (1)(i) and (v) to reconstruct a section of the Siegfried-East Palmerton #1 and #2 138/69 kV Transmission Line (Siegfried-East Palmerton).
The Petition concerns a section of the Siegfried-East Palmerton, two associated transmission line taps, and PPL Electric’s plan to rebuild them (Proposed Project).  The subject section of the transmission line is a combination of one double-circuit line and two parallel single-circuit lines which span from a point where the existing Siegfried-East Palmerton transmission line and Siegfried – Hauto #1 and #4 138/69 kV Transmission Line diverge (the Split) in Washington Township, Lehigh County to the East Palmerton 
230-69 kV Substation (East Palmerton Substation) in Lower Towamensing Township, Carbon County. 

In its Petition, PPL Electric explains that a portion of the rebuilt Siegfried-East Palmerton will be located on new right-of-way (ROW).  PPL Electric states that the entire Proposed Project could be constructed entirely within the existing ROW.  However, PPL Electric has recently acquired new voluntary ROW to accommodate a request from Lehigh Gap Nature Center to shift the transmission line in order to minimize impacts on its property.  To facilitate this, PPL also voluntarily acquired new ROW from two other property owners, Lehigh County and East Penn Township.  None of the affected property owners objected to shifting the location of the line into the new ROW.


PPL Electric states that a key component of its ability to complete the transmission line project on schedule is the waiver of the formal application requirement in 52 Pa. Code § 57.72(a) et seq.  In its Petition, PPL Electric requests that it be allowed to file a letter of notification in lieu of an application for the project.


Section 57.72(d) sets forth the circumstances under which a letter of notification in lieu of an application for the construction of an HV line may be granted:


(d)
Letter of notification in lieu of an application:



(1)
A letter of notification may be filed with the Commission in lieu of the 




application process set forth in §§ 57.71-57.76 for the following:

(i) An HV line which is proposed to be located entirely on an existing transmission line right-of-way, so long as the size, character design or configuration of the proposed HV line does not substantially alter the right-of-way.

(ii) An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within the applicant’s existing transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present levels, so long as the size, character, design or configuration of the proposed line does not substantially alter the right-of-way.

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(vi) An HV line having a proposed route of 2 miles or less.

In addition, waiver of the specific requirements of the Commission’s Transmission Line Siting Regulations, at 52 Pa. Code § 57.71 et seq., is provided for in § 57.72(e):

(e)
The Commission or the presiding officer may – upon the petition of any party, upon the Commission’s own motion, or upon the presiding officer’s own motion – waive one or more or all of the requirements in this subchapter.  The petition shall clearly state the requirement sought to be waived and the reason therefore.

The Proposed Project nearly satisfies the criteria to file a letter of notification.  While

the Proposed Project does not fit the technical requirements of the exceptions outlined in 

§ 57.72(d), inasmuch as the project nearly meets several of the exceptions § 57.72(d)(1)(i), (v) and (vi), waiver of the strict application of § 57.72(d)(1)(i) and (v), and permission to file a letter of notification is nevertheless appropriate.  

In particular, the entire line reconstruction is approximately 6.9 miles in length, and, while that length exceeds the two-mile standard to file a letter of notification found in § 57.72(d)(1)(vi), the new construction comprises only about six percent of the total construction.  All but 0.4 miles of the approximately 6.9-mile reconstruction project will be rebuilt entirely within the existing ROW of the Siegfried-East Palmerton and two associated taps.  The 0.4-mile diversion will be located within newly acquired ROW, adjacent to the existing ROW and was obtained at the request of a landowner.  PPL Electric further states that the project will consolidate approximately 4.0 miles of existing transmission line from two parallel single-circuit lines to one double-circuit line.  The average structure height is increasing, however, the total number of structures within the ROW is decreasing by approximately 50.

PPL Electric states that the reconstructed Siegfried-East Palmerton will not have significant incremental impacts on the existing ROW for the following reasons:

(a) The line will be constructed entirely within the existing right-of-way, except for a 0.4-mile stretch where the new ROW was acquired at the request of the property owner.

(b) Approximately 4.0 miles of the existing transmission line will be consolidated from two parallel single-circuit lines to one double-circuit line.

(c) The average structure height is increasing by approximately 30 feet and the total number of structures is decreasing within the existing ROW.

(d) The new structures will be placed in close proximity to the existing structures.

(e) No structures will be placed on a property that does not already have an existing pole. 
The Commission’s Transmission Line Siting Regulation specifically provides 

for waivers of a specific siting regulation.  52 Pa. Code § 57.72(e).  The Commission believes that the waiver request of PPL Electric is warranted.  No protests were filed and granting the waiver would not be inconsistent with applicable law or Commission Policy and precedent regarding transmission line siting.


The majority of the line is located within the ROW of an existing transmission line and also includes construction within 0.4 miles of new ROW.  Although the entire Proposed Project would not fit into one of the HV line categories, each of the three individual components of the Proposed Project, on their own, would qualify for the use of a Letter of Notification under 52 Pa. Code § 57.72(d)(1)(i), (v), and (vi).  Therefore, we are granting PPL Electric’s request for a waiver of certain provisions set forth at 52 Pa. Code § 57.71 et seq.
Letter of Notification


Copies of the LON were served in accordance with Section 57.72(d)(3), and as set forth in 52 Pa. Code § 57.74(b)(c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Lehigh and Carbon County Commissioners, Borough of Palmerton and Washington, Lower Towamensing, and East Penn Townships, et al.  No protests were filed.  No hearings were held.

As stated above, the Commission grants the Petition of PPL Electric and waived its regulations at 52 Pa. Code §§ 57.72(d)(i) and (v) to allow PPL Electric to file an LON in lieu of an application for authorization to reconstruct the high voltage line described in the Petition and the subject of this LON.  This filing qualifies as an LON based only on Commission approval of PPL Electric’s Petition for Waiver in accordance with 
52 Pa. Code § 57.72(e). 
PPL Electric requests approval to rebuild approximately 6.9 miles of 138/69 kV transmission line in Washington Township, Lehigh County and the Borough of Palmerton and Lower Towamensing and East Penn Townships, Carbon County, Pennsylvania.  The subject section of transmission line is part of the Siegfried-East Palmerton including the associated Palmerton 138/69 kV Tap (Palmerton Tap) and Palmerton Zinc 138/69 kV Tap (Palmerton Zinc Tap). The entire section of transmission line to be rebuilt will be collectively referred to as the Siegfried-East Palmerton.  

PPL Electric states that rebuilding the Siegfried-East Palmerton is necessary to modernize the lines to meet all current design and lightning protection standards and to help ensure reliable and continuous service to customers in Lehigh and Carbon Counties.  PPL Electric further states that an independent field investigation and assessment was conducted by a third party and revealed that the aging Siegfried-East Palmerton transmission line facilities are showing signs of significant deterioration.  The assessment concluded that the lines are reaching the end of their reliable service life (approximately 70 years) and that replacing the lines, rather than refurbishment, was the cost-effective solution.  PPL Electric further states that Palmerton Tap and Palmerton Zinc Tap need to be rebuilt to operate at 138 kV standards.
PPL Electric states that the lines traverse heavily industrialized areas which have accelerated the corrosion rate of the steel structures and associated hardware on the lines.  Specifically, the assessment identified surface corrosion on tower steel with failing coatings and exposed galvanizing causing corrosion to increase at an accelerated rate.  PPL Electric further states that contamination has accumulated on the surface of the insulators and is reducing their insulating properties.  The assessment also identified many of the wood poles as being in a severe condition resulting from being directly imbedded in marsh and wet areas and from woodpecker damage. 

PPL Electric uses an Asset Optimization Strategy to systematically identify and modernize its aging facilities.  The measures used to identify equipment and lines that qualify for this work include age, condition, criticality of the equipment or line, and circuit performance.
PPL Electric states that the Proposed Project includes the replacement of all conductors and the wood and steel lattice transmission structures on the Siegfried-East Palmerton with a single high capacity double-circuit 138/69 kV transmission line.  The project also includes the installation of a dual optical ground wire and load break air break switches.  

PPL Electric states that the Proposed Project is phase two of a three phase project.  The overall project includes the replacement of the transmission lines between the Siegfried Substation and the East Palmerton and Hauto Substations.  Phase one which includes rebuilding the Hauto-Siegfried 138/69 kV Transmission Line from the Split to the Siegfried Substation was previously approved by the Commission.
  However, construction was deferred to align work on phase one with other work in the area.  Phase three includes rebuilding approximately 15.2 miles of the Hauto-Siegfried #1 and #2 69 kV Transmission Line from the Hauto 69-12 kV Substation to the Split.
PPL Electric states that the Siegfried-East Palmerton transmission line rebuild will ensure continued reliable service by bringing the transmission line into compliance with current design standards and providing increased lightning protection to reduce the frequency of momentary outages.  PPL Electric states that the load break air break switches will allow for sectionalizing of the transmission system to restore service to customers in instances of sustained outages or maintenance scenarios.  PPL Electric states that the existing structures and conductors will be replaced with steel monopoles and conductors with greater ampacity.  PPL Electric further states that the line will initially be operated at 69 kV and will be increased to 138 kV when the additional capacity is needed.  The Proposed Project was presented at a PJM Mid-Atlantic Sub Regional Transmission Expansion Planning (RTEP) meeting and was approved as supplemental project s0525 in the PJM RTEP.
The Siegfried-East Palmerton #1 & #2 138/69 kV Transmission Line is approximately 6.9 miles in length and primarily consists of 124 wood poles and steel lattice transmission line structures constructed around 1950.  The Palmerton Tap and Palmerton Zinc Tap were constructed around the same time, are approximately 0.1 and 0.06 miles in length respectively and combined consist of six wood transmission line structures.  PPL Electric states that it will remove the existing structures and install 80 new steel monopole structures.  The existing structures range in height from 35 to 110 feet with an average height of about 65 feet.  The new steel structures will average approximately 95 feet in height.  The new poles will be self-supported, either directly embedded or on concrete caisson foundations.  The new monopoles are anticipated to have a service life of approximately 70 years.
In its filing, PPL Electric states that the Proposed Project has been designed and will be built within new and existing ROW of the Siegfried-East Palmerton.  The existing ROW varies from centerline rights to approximately 150 feet and is generally 100 feet in width.  PPL Electric further states that approximately 0.4 miles of the ROW will be shifted.  The new ROW will be approximately 100 feet in width.
PPL Electric maintains the project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  
Under the Commission’s siting regulations at 52 Pa. Code § 57.71 et seq., the company must establish a clear need for the project
 and demonstrate that the proposed solution is an efficient and cost-effective choice relative to other alternatives.
  The Company, at this time, has not provided sufficient information to meet these criteria.

Commission staff data requests to PPL potentially contradict the above assessment of the reliability of this line.  First, PPL disclosed that, over the last 5 years, this transmission line only had one outage, associated with only one customer.  Further, the independent field investigation was limited to a statistically insignificant sample size (eight).  The sample set selected for independent field investigation included two types of samples: 1) structures that PPL selected, known to have had historical maintenance issues that were previously addressed or that were critical structures (e.g. road crossings), and 2) a random sampling that the assessor, DGA, selected from the remainder of the line.  Of the 8 sample structures selected, 6 of them were selected by PPL and 2 of them were selected by DGA.  Such a small sampling of mostly non-random facilities does not present adequate information as to the state of the facilities.  Further, the almost perfect performance of the facilities appears to contradict PPL’s assessment of reliability.  Lastly, PPL acknowledges that the impact on CAIDI/SAIDI/SAIFI is negligible.

As to examination of available alternatives, PPL asserts that replacing the lines, rather than refurbishment, was the cost-effective solution.  Data requests revealed that operation and maintenance (O&M) of the line ranged from $23,000 to $300,000 per year.  PPL also provided a lower cost estimate of $15.9 million for the complete rehabilitation of the line.  PPL fails to provide any analysis as to the cost of the alternative solutions, the complete rehabilitation of the line or the current O&M costs of the existing system, relative to the proposed new $23.6 million system.  While replacement of the system may be needed at some point, PPL did not provide the necessary support to justify complete replacement at this time.

Based on the discussion above, we deny, without prejudice, the proposed LON application as it stands.  While the Commission’s regulations at 52 Pa. Code § 57.72(d)(5) limit PPL’s recourse upon denial of a LON application to filing a full siting application, we are willing to waive that requirement, pursuant to 52 Pa. Code §57.72(e), and allow the company some flexibility in determining whether its best course of action is to submit a revised LON or file a full siting application, should the Company seek future approval of the Proposed Project.  PPL’s new filing should provide additional support that this project is an optimal means to maintain reliability on its transmission and distribution system in a cost-effective manner.  THEREFORE,

IT IS ORDERED:

1. That the Petition of PPL Electric Utilities Corporation for the waiver of certain provisions of the Commission’s Regulations for Commission Review of Siting and Construction of Electric Transmission Lines set forth at 52 Pa. Code § 57.71 et seq. is hereby approved.
2. That the Letter of Notification filed by PPL Electric Utilities Corporation, for approval to rebuild approximately 6.9 miles of 138/69 kV transmission line in Washington Township, Lehigh County and the Borough of Palmerton and Lower Towamensing and East Penn Townships, Carbon County, Pennsylvania is denied, without prejudice. 
3. That PPL Electric Utilities Corporation comply with the application process set forth in 52 Pa. Code § 57.72(d)(5) or file a new Letter of Notification application, consistent with the direction of this Order.

4. That upon completion of Ordering Paragraph 3, this proceeding at Docket No. A-2018-3001477 be closed. 
[image: image1.png]


BY THE COMMISSION,
Rosemary Chiavetta

Secretary

ORDER ADOPTED: September 20, 2018
ORDER ENTERED:  October 10, 2018
� A-2013-2372112 – Letter of Notification of PPL Electric Utilities Corporation, filed pursuant to 52 Pa. Code Chapter 57.72(d)(1)(i),(iv) and (vi), with respect to replacement of two existing 69 kV Lines with the Siegfried-Hauto #1 & #2 138/69 kV Transmission Line and the construction of the Treichlers 138/69 kV Taps in Allen Township, Northampton County and North Whitehall and Washington Townships, Lehigh County, Pennsylvania; Order entered 


September 12, 2013


� 52 Pa. Code §57.72(5) states that an application shall contain a general statement of the need for the proposed HV line in meeting identified present and future demands for service, of how the proposed HV line will meet that need and of the engineering justifications for the proposed HV line. 


� 52 Pa. Code §57.76(a)(4) requires that the Commission finds and determines that a proposed HV line… will have minimum adverse environmental impact, considering the electric power needs of the public, the state of available technology and the available alternatives.  Also see, generally, Energy Conservation Council of Pennsylvania v. PUC, 995 A2.d 465 (Pa. Cmwlth. 2010).





5

