|  | COMMONWEALTH OF PENNSYLVANIA PENNSYLVANIA PUBLIC UTILITY COMMISSION 400 NORTH STREET, HARRISBURG, PA 17120 | IN REPLY PLEASE REFER TO OUR FILE |
| --- | --- | --- |

October 29, 2019

Docket No. A-2019-3012304

Utility Code: 110500

CERTIFIED

JESSICA R ROGERS

POST & SCHELL P C

17 NORTH SECOND STREET 12TH FLOOR

HARRISBURG PA 17101-1601

Re:  	Letter of Notification of PPL Electric Utilities Corporation for Approval to Site and Construct 230 kV Transmission Lines in Luzerne County, Pennsylvania.

Dear Ms. Rogers:

On August 19, 2019, PPL Electric Utilities Corporation (PPL Electric) filed a Letter of Notification (LON) for approval to site and construct 230 kV Transmission Lines in Salem Township, Luzerne County, Pennsylvania.  In order for us to complete our analysis of the subject application, the Bureau of Technical Utility Services requires answers to the enclosed data requests.  This information is necessary for completion of our review of the filing.

Please be advised that you are directed to forward the requested information to the Commission within ten (10) days of receipt of this letter.  Failure to respond may result in the LON being denied.  As well, if PPL Electric has decided to withdraw its filing, please reply notifying the Commission of such a decision.

Please forward the information to the Secretary of the Commission at the address listed below.  When submitting documents, all documents requiring notary stamps must have original signatures.  Please note that some responses may be e-filed to your case, http://www.puc.pa.gov/efiling/default.aspx.  A list of document types allowed to be e-filed can be found at http://www.puc.pa.gov/efiling/DocTypes.aspx.

Rosemary Chiavetta, Secretary

Pennsylvania Public Utility Commission

400 North Street

Harrisburg, PA 17120

Your answers should be verified per 52 Pa Code § 1.36.  Accordingly, you must provide the following statement with your responses:

I, ________________, hereby state that the facts above set forth are true and correct to the best of my knowledge, information and belief, and that I expect to be able to prove the same at a hearing held in this matter.  I understand that the statements herein are made subject to the penalties of 18 Pa.C.S. § 4904 (relating to unsworn falsification to authorities).

The blank should be filled in with the name of the appropriate company representative, and the signature of that representative should follow the statement.

In addition, to expedite analysis of the LON, please also e-mail the information to

Jordan Van Order at jvanorder@pa.gov.  Please direct any questions to Jordan Van Order, Bureau of Technical Utility Services, at jvanorder@pa.gov (preferred) or 717-787-8763.

Sincerely,

Rosemary Chiavetta

Secretary

Enclosure

Bureau of Technical Utility Services

Data Requests

Docket No. A-2019-3012304

Note:  If any responses contain Confidential Security Information (CSI),

please inform TUS staff via phone call or email.

A-16	Reference the Letter of Notification, Paragraph 23.  Please provide the approximate length of 69 kV transmission line to be rebuilt.

A-17	Reference the Letter of Notification, Paragraph 28.  Please provide the approximate height of existing nearby transmission line structures on the Montour-Susquehanna and Montour-Susquehanna T10 230 kV transmission lines.

A-18	Reference the Letter of Notification, Attachment 1, Page 3.  Please explain whether the subject 69 kV facilities are part of the bulk electric system.  If not, please explain why PPL Electric is applying NERC standards to these facilities.

A-19	Reference the Letter of Notification, Attachment 1, Section 4.0.  Alternative 1 and Alternative 2 appear to require rebuilding all of the 69 kV lines serving the Berwick area rather than only the Hunlock-Berwick 69 kV Transmission Line.  Please explain.

A-20	Reference TUS Data requests, Response to A-1.  Please provide a detailed explanation as to why PPL Electric’s 69 kV voltage drop limit is more restrictive than the PJM Baseline limit of 10%.

A-21	Reference TUS Data Requests, Response to A-1.  The allowable voltage drop on the 69 kV systems neighboring PPL Electric appears to vary from 7% to 10%.  Please explain why PPL Electric’s voltage drop limit is a more restrictive 8%.

A-22	Reference TUS Data Requests, Response to A-4.  Please explain when the alleged thermal violation was identified.

A-23	Reference TUS Data Requests, Response to A-4.  Please explain whether the additional 4,600 MW of generation is specific to the area in which the alleged violation occurs or whether it is across the entire PPL Electric transmission footprint.

A-24	Reference TUS Data Requests, Response to A-4.  Please explain whether the new generator(s) responsible for the thermal violation are responsible for any portion of the costs associated with the required upgrades.  If not, please provide a detailed explanation as to why.