# PENNSYLVANIA

# PUBLIC UTILITY COMMISSION

# Harrisburg, PA 17105-3265

# Public Meeting held April 16, 2020

Commissioners Present:

Gladys Brown Dutrieuille, Chairman

David W. Sweet, Vice Chairman

Andrew G. Place

John F. Coleman, Jr.

Ralph V. Yanora

| Petition of Pennsylvania-American Water Company – Wastewater Division for Approval of its Modified Long-Term Infrastructure Improvement Plan | Docket Number: P-2014-2431005 |
| --- | --- |

# OPINION AND ORDER

BY THE COMMISSION:

Before the Commission for consideration is the Petition for approval of its Modified Long-Term Infrastructure Improvement Plan (Modified LTIIP) of Pennsylvania-American Water Company – Wastewater Division (PAWC-WD).  PAWC-WD filed its Petition on December 12, 2018.  As detailed below, PAWC-WD filed an amended Modified LTIIP pursuant to a Commission Order entered January 7, 2020.  Copies of the Petition and amended Modified LTIIP were served on the statutory advocates and the parties of record from PAWC-WD’s most recent base rate case proceeding.

HISTORY OF THE PROCEEDING

On December 12, 2018, PAWC-WD filed the instant Petition seeking review and approval by the Commission.

On January 2, 2019, the Commission’s Bureau of Investigation and Enforcement (BIE) filed an Answer to PAWC-WD’s Petition.  In its Answer, I&E requested that the matter be assigned to the Commission’s Office of Administrative Law Judge (OALJ) for an investigation and, if necessary, evidentiary hearings.  BIE stated its intent to participate in the proceeding to ensure that the proposed Modified LTIIP would meet the legal requirements of the Public Utility Code, the Commission’s Regulations and Pennsylvania law.  BIE also stated that it was participating in this proceeding to ensure that the interests of all PAWC-WD ratepayers were protected.

On January 9, 2019, the Office of Consumer Advocate (OCA) filed Comments.  In its Comments, the OCA recommended that PAWC-WD provide additional information relating to the 2018 Petition to Modify LTIIP.  OCA also recommended that PAWC-WD take certain actions in future LTIIP related filings.

On January 10, 2019, BIE filed an Amended Answer to the PAWC-WD’s Petition.  In the Amended Answer, BIE asserted that there were specific material factual issues that must be referred to the OALJ for disposition.

By Notice dated February 8, 2019, the matter was assigned to OALJ by the Commission.

On August 15, 2019, PAWC-WD, BIE, OCA, and the Office of Small Business Advocate (Joint Petitioners) filed a Joint Petition for Settlement (Settlement) that proposed to resolve all contested issues in the proceeding.

On September 30, 2019, the Joint Petitioners filed a Joint Stipulation of Facts regarding the matter.

By Order dated October 23, 2019, the Joint Stipulation of Facts was approved and admitted into the record.

The Recommended Decision of Administrative Law Judges Joel Cheskis and Andrew Calvelli was issued on November 26, 2019, which recommended approval of the Settlement.  On December 19, 2019, the Commission adopted a Joint Motion that, inter alia, adopted the Recommended Decision, but required PAWC-WD to file an amended Modified LTIIP with the Commission’s Bureau of Technical Utility Services incorporating matters expressly resolved by the Settlement.  The Commission entered an Order on January 9, 2020, pursuant to the Joint Motion.

On January 30, PAWC-WD filed its amended Modified LTIIP.  No comments were filed to the amended Modified LTIIP.  BIE and OCA had opportunity to address any concerns of their comments through the adjudication process and Settlement negotiation, and no new comments were filed to the amended Modified LTIIP.  Therefore, we shall not address the comments any further in this Order.

BACKGROUND

On February 14, 2012, Governor Corbett signed into law Act 11 of 2012, (Act 11), which amends Chapters 3, 13 and 33 of Title 66.  Act 11, inter alia, provides jurisdictional water and wastewater utilities, electric distribution companies (EDCs), and natural gas distribution companies (NGDCs) or a city natural gas distribution operation with the ability to implement a DSIC to recover reasonable and prudent costs incurred to repair, improve or replace certain eligible distribution property that is part of the utility’s distribution system.  The eligible property for the utilities is defined in 66 Pa. C.S. §1351.  Act 11 states that as a precondition to the implementation of a DSIC, a utility must file a LTIIP with the Commission that is consistent with 66 Pa. C.S. §1352.

The Commission promulgated regulations relating to LTIIPs at 52 Pa. Code §§ 121.1 – 121.8 that became effective December 20, 2014.  In accordance with the regulations, a wastewater company must include the following elements in its LTIIP:

- Types and age of eligible property;

- Schedule for its planned repair and replacement;

- Location of the eligible property;

- Reasonable estimates of the quantity of property to be improved;

- Projected annual expenditures and measures to ensure that the plan is cost      effective;

- Manner in which replacement of aging infrastructure will be accelerated and how repair, improvement or replacement will maintain safe and reliable service;

- A workforce management and training program; and

- A description of a utility’s outreach and coordination activities with other utilities, the Department of Transportation (PennDOT) and local governments on planned maintenance/construction projects.

PAWC-WD’S MODIFIED LTIIP

PAWC-WD, Utility Code 230073, is a wholly owned subsidiary of American Water Works Company, Inc., and an affiliate of Pennsylvania-American Water Company (PAWC), utility Code 212285.  PAWC and PAWC-WD provide public utility water and sewer service to residents in Pennsylvania.  PAWC-WD owns and operates 18 wastewater systems located in 12 Counties across the Commonwealth and serves approximately 65,139 customer connections, including several bulk municipal customers.  PAWC-WD’s current LTIIP was approved in a Commission Order entered December 4, 2014, at Docket Number P-2014-2431005.

PAWC-WD’s current LTIIP spanned the years 2015 through 2019.  PAWC-WD’s Modified LTIIP proposes to replace year 2019 and further expand the LTIIP to include the years 2020 through 2023.  PAWC-WD’s Modified LTIIP also adds certain wastewater assets from systems acquired by PAWC-WD since 2014.  The Modified LTIIP utilizes a risk-based condition approach in order to cost-effectively prioritize wastewater collection system replacement and rehabilitation projects and accelerates the rehabilitation, improvement and replacement of aging wastewater infrastructure for wastewater systems.

PAWC-WD states that the focus of the Modified LTIIP is to replace or rehabilitate collection system infrastructure based on strategic condition assessment and hydraulic evaluations.  PAWC-WD intends to reduce infiltration and inflow (I&I) levels to address Sanitary Sewer Overflow (SSO) and Combined Sewer Overflow (CSO) issues, and to correct deficiencies in certain newly acquired wastewater systems.  PAWC-WD notes that these types of system improvements will improve system safety and reliability, customer service, and environmental compliance.

PAWC-WD maintains that I&I has been reduced in several areas since the Wastewater DSIC rate mechanism was implemented.  PAWC-WD notes that after significant capital investments in collection system upgrades, which occurred over multi- year timeframes, its Clarion collection system no longer experiences SSO events.  PAWC-WD also notes that after a complete rebuild of the Marcel Lake collection system, the system experienced a dramatic reduction in I&I.

PAWC-WD notes that accelerated infrastructure replacement and rehabilitation is needed to continue meeting the challenges of its wastewater systems, including systems that have been acquired since its current LTIIP was submitted in 2014.  PAWC-WD notes that its wastewater customer base has increased significantly from approximately 16,803 connections in 2014, to the current total of 65,139 customer connections.  PAWC-WD maintains that newly acquired systems such as Scranton, McKeesport, Duquesne, and Dravosburg are currently under Pennsylvania Department of Environmental Protection (DEP) Consent Orders and require accelerated rehabilitation and replacement.

PAWC-WD, in their petition, addressed the 8 LTIIP elements required by 52 Pa. Code § 121.3, as discussed below:

(1) TYPES AND AGE OF ELIGIBLE PROPERTY

PAWC-WD’s Position

PAWC-WD reports that its wastewater collection systems are comprised of approximately 65,139 service laterals, 20,874 manholes, and 4,156,078 linear feet (LF) of gravity main, which includes combined sewer gravity mains.  PAWC-WD in its Petition provided substantial detail on its system components including: the material composition, length, and age of its pipes and mains; lift stations; manholes; and service laterals.

PAWC-WD states that the condition of their wastewater systems varies, depending on age, material, local conditions and quality of initial design or installation.  PAWC-WD notes that some systems require significant capital investment to maintain efficient, safe, and reliable service for existing customers.  PAWC-WD acknowledges that it has acquired its wastewater systems from prior ownership in various states of disrepair.  PAWC-WD notes that many of its systems have aging infrastructure and significant I&I from rainfall runoff and groundwater.

PAWC-WD reported that it owns the following types of sewer collection systems:

Gravity Systems – PAWC-WD states that its gravity main and manhole material generally depends on installation date.  PAWC-WD maintains that newer mains are polyvinyl chloride (PVC) and older mains are mostly vitrified clay pipe (VCP).  PAWC-WD notes that its newer manholes are pre-cast or cast in place concrete and older manholes are brick.  However, PAWC-WD’s Modified LTIIP notes that 53.8% of the gravity main material is unknown.  In additional information filed with the Commission, PAWC-WD notes that it has two paths it can take to reduce the amount of unknown materials.  One path is through regular maintenance where the material and condition of the pipe is logged and entered in its data base.  The other path occurs when PAWC-WD acquires a system.  As part of its evaluation process, much of the system is cleaned and inspected.  PAWC-WD notes that condition assessment of its pipes and manholes is done at that time along with a notation of types of material found.

PAWC-WD’s Modified LTIIP indicated that it deemed the entire customer service lateral on a gravity collection to be DSIC-eligible property.  In supplemental information filed with the Commission, PAWC-WD clarified that it does not plan to replace or line customer-owned portions of the service laterals in a gravity system.  However, it notes that when there is high influent at the connection of a service lateral to the sewer main the company may replace a portion of the service lateral to remedy or reduce the influent flow.  PAWC-WD notes that this work is done either through the installation of a "top-hat" washer type used in plumbing for tap fitting or through physical work on that portion in the right-of-way.

Low Pressure Systems – PAWC-WD reports that on its low-pressure systems, the eligible property associated with the service lateral extends from the sewer main to the individual customer’s grinder pump unit.  PAWC-WD notes one exception to this exists in the Blue Mountain district where there are 5 company grinder pumps and pit installations.  PAWC-WD states that it owns approximately 458,177 LF of low-pressure sewer mains.

Force Main Systems – PAWC-WD reports that a force main is a pressurized discharge pipeline from a lift station.  PAWC-WD notes that a force main pipeline may contain in-line flow meters, valve vaults, and air and vacuum release chambers.  PAWC-WD states that it owns and operates 95 lift stations and approximately 257,725 LF of force main collectively.  PAWC-WD states that in general, its force main material is cast iron for older pipes and ductile iron or PVC for newer pipes.

Table 1 and Table 2, below, detail certain classes of eligible property for each wastewater system.

Table 1 – Types and Age of Eligible Property

| Wastewater System |  | Gravity Main (LF) | Combined Sewer Gravity Main (LF) | Force Main / Low Pressure Main (LF) | Lift Stations | Manholes | Service Laterals a | General System Age |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Central | Fairview North | 165,600 | 0 | 18,844 | 11 | 869 | 1,498 | >1950 |
|  | Fairview South | 198,722 | 0 | 13,068 | 6 | 1,050 | 2,498 | >1992 |
|  | Franklin | 55,239 | 0 | 12,423 | 1 | 198 | 348 | >1972 |
|  | McEwensville | 12,669 | 0 | 1,242 | 4 | 57 | 133 | >1984 |
|  | New Cumberland | 144,692 | 0 | 6,898 | 3 | 608 | 3,066 | >1950 |
| Northeast | Blue Mountain Lake | 0 | 0 | 68,250 | 6 | 0 | 830 | >1990 |
|  | Lehman Pike | 0 | 0 | 268,447 | 13 | 0 | 2,714 | >1980 |
|  | Marcel Lake | 30,732 | 0 | 28,597 | 3 | 130 | 354 | >1980 |
|  | Pocono | 150,648 | 0 | 99,795 | 2 | 777 | 3,689 | >1975 |
|  | Scranton | 552,748 | 1,186,820 | 12,032 | 7 | 9,055 | 29,551 | >1900 |
| Southeast | Coatesville | 352,945 | 0 | 93,605 | 17 | 1,670 | 6,226 | >1930s |
| West | Clarion | 200,860 | 0 | 36,293 | 6 | 930 | 2,157 | >1930s |
|  | Claysville | 62,082 | 0 | 1,149 | 1 | 342 | 503 | >1983 |
|  | Koppel | 25,909 | 0 | 0 | 0 | 87 | 351 | >1920s |
|  | McKeesport | 73,403 | 616,877 | 32,731 | 9 | 3,236 | 8,096 | >1900 |
|  | Dravosburg | 19,604 | 32,544 | 1,219 | 1 | 308 | 625 | >1900 |
|  | Duquesne | 59,963 | 124,596 | 0 | 0 | 1,125 | 1.840 | >1900 |
|  | Paint-Elk | 89,425 | 0 | 21,310 | 5 | 432 | 660 | >1960s |
| TOTAL |  | 2,195,241 | 1,960,837 | 715,902 | 95 | 20,874 | 65,139 |  |

* PAWC-WD is not including the customer-owned portion of the service lateral as DSIC eligible property.  Only the portion of the service lateral owned by PAWC-WD is included in the scope of replacement/rehabilitation.

Table 2 – Types of Eligible Property for Combined Sewer Systems

| System | CSO Structures | Diversion Chambers | Inlets / Catch Basins |
| --- | --- | --- | --- |
| Scranton | 70 | 4 | 3,013 |
| McKeesport | 26 | 4 | 1,852 |
| Dravosburg | 1 | 0 | 264 |
| Duquesne | 4 | 0 | 944 |

Comments

No comments were received regarding the types and age of eligible property.

Resolution

As noted on page 7, above, PAWC-WD indicates that 53.8% of the gravity main material is unknown.  PAWC-WD has outlined methods to reduce the amount of unknown material and it is important that Commission staff and other interested parties be updated on the progress of identification of main material in PAWC-WD’s gravity system, as well as its other systems.  Therefore, PAWC-WD, beginning with its Annual Asset Optimization Plan (AAOP) for calendar year 2020, shall include updated information on its pipeline materials and diameters for all its wastewater systems.

Upon review of PAWC-WD’s Modified LTIIP, as amended, and any supplemental information filed, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code § 121.3(a)(1) by identifying the types and ages of eligible property for which it seeks DSIC recovery.

(2) SCHEDULE FOR PLANNED REPAIR AND REPLACEMENT OF ELIGIBLE PROPERTY

PAWC-WD’s Position

PAWC-WD states that it will utilize a risk-based condition assessment approach to schedule planned repairs and replacements of eligible property.  PAWC-WD maintains that it follows a condition-based risk assessment prioritization system developed by the National Association of Sewer Service Companies (NASSCO) that can be applied to score and rank projects in different wastewater systems against each other to ensure cost-effective prioritization of capital investment.  PAWC-WD states that its risk-based management approach allows for proactive planning.   PAWC-WD maintains that the scoring system has flexibility by allowing adjustments in how each criterion is weighted, and accounts for special circumstances which may be difficult to quantify.  PAWC-WD states that this model will help develop a schedule for planned rehabilitation and replacement of eligible property in order to maintain safe, reliable service to existing customers.

PAWC-WD states that it will perform a GIS analysis to assign a risk score to each likely project to accomplish this prioritization.  PAWC-WD defines risk as: Risk = Likelihood of Failure (LoF) x Consequence of Failure (CoF).  PAWC-WD notes that the first step of the planning process is to conduct a macro-level overview of each wastewater system to help identify areas of concern which may contain properties in need of replacement.  PAWC-WD states that its macro-level planning process helps identify groups of assets that are potential candidates and those groups of assets that are unlikely to need near-term replacement.  PAWC-WD maintains that the macro-level planning allows resources required for micro-level planning to be more efficiently targeted to those areas most likely to contain aging infrastructure in need of rehabilitation or replacement.

PAWC-WD states that the next step in its planning process is to conduct a more detailed, micro-level planning analysis.  PAWC-WD notes that it conducts a comprehensive sewer system evaluation which is its systematic approach to identify specific properties to be rehabilitated or replaced.  PAWC-WD maintains that during the micro-level planning process, specific properties are identified as candidates for replacement or rehabilitation using a risk-based methodology based on a condition assessment and hydraulic capacity evaluation.

PAWC-WD states that its strategic improvements identified in the micro-level planning process can be grouped in the following categories:

Manhole replacement / rehabilitation – PAWC-WD advised that work in this category may include frame and cover replacement, internal grouting, lining, or complete replacements.  PAWC-WD notes that manhole lining can be used for structural reinforcement, reduction of groundwater infiltration, or protection from corrosive gases.  PAWC-WD maintains that various factors, such as location, structural integrity, and manhole depth determine whether replacement or rehabilitation is best.

Pipe replacement / rehabilitation – PAWC-WD advised that work in this category  may consist of the following: complete replacements, partial replacements, or trenchless rehabilitation such as cured-in-place pipe lining (CIPP), slip lining, close-fit pipe lining (fold and form), other pipe coatings/lining systems, pipe bursting, horizontal directional drilling using fused high-density polyethylene (HDPE) pipe or fused PVC pipe.

Service lateral replacement / rehabilitation – PAWC-WD advised that work in this category may consist of replacing or rehabilitating gravity or low-pressure sewer laterals, including taps, and cleanouts.  PAWC-WD notes that a cured-in-place liner is a trenchless alternative that may be best for service laterals that are difficult to excavate.  PAWC-WD states that depending on the condition and number of connections, service lateral replacements may be combined with main line replacement / rehabilitations.

Through a data request, Commission staff asked PAWC-WD for clarification on its plans to replace or line service laterals.  In supplemental information filed with the Commission, PAWC-WD advised that it does not plan to replace or line customer-owned portions of the service lateral.

Lift station replacement / rehabilitation – Lift stations are evaluated on a case by case basis.  A scoring system is provided at the end of this Section.  Necessary improvements can usually be completed by full or partial rehabilitation.  Replacement may be the best option for older and outdated lift stations.

Combined sewer overflow facility replacement / rehabilitation – CSO facilities are evaluated on a case by case basis.  Replacement or rehabilitation of these facilities may include features such as outfall structures, bar screens, piping, valves, or diversion chamber / flow weirs.

PAWC-WD notes that once specific properties are identified as needing replacement or rehabilitation, the final step in the micro-level planning process is prioritization.  PAWC-WD states that it plans to apply a prioritization model to score capital improvement projects which will be funded through the wastewater DSIC program.  PAWC-WD’s prioritization model for wastewater collection mains will use pipe condition information to assess the system’s ability to meet performance measures.  PAWC-WD maintains that the list of identified projects will cover multiple wastewater systems and geographical areas across the Commonwealth.

In supplemental information filed with the Commission, PAWC-WD outlined the projected schedule for completion of the Company’s risk-based condition assessment for each wastewater system covered by the LTIIP.   Table 3, below, is organized by 3 categories of systems: (1) newly acquired systems; (2) systems subject to a DEP or United States Environmental Protection Agency (EPA) Consent Order; and (3) all other “routine” systems that do not fall under the other two categories.

Table 3 – Condition Assessment Schedule

| District | Total Gravity LF | 2018 | 2019 | 2020 | 2021 | 2022 | # Manholes |
| --- | --- | --- | --- | --- | --- | --- | --- |
| New Acquisitions |  |  |  |  |  |  |  |
| Franklin | 55,239 |  | 55,239 |  |  |  | 198 |
| McEwensville | 12,669 |  | 12,669 |  |  |  | 57 |
| New Cumberland | 144,692 |  | 56,900 | 87,792 |  |  | 608 |
| Fairview North | 165,600 | 159,505 | 6,095 |  |  |  | 869 |
| Fairview South | 198,722 |  | 45,940 | 152,782 |  |  | 1,050 |
| Paint Elk | 89,425 |  | 5,000 | 0 | 0 |  | 432 |
| Marcel Lakes | N/A |  |  |  |  |  | N/A |
| Consent Order |  |  |  |  |  |  |  |
| Scranton | 1,739,568 | 363,000 | 609,000 | 767,568 | 0 |  | 9,055 |
| McKeesport | 690,280 |  | 552,224 |  |  |  | 3,236 |
| Dravosburg | 52,148 |  | 52,148 |  |  |  | 308 |
| Duquesne | 184,559 |  | 184,559 |  |  |  | 1,125 |
| Routine |  |  |  |  |  |  |  |
| Blue Mountain | 0 |  |  |  |  |  | 0 |
| Claysville | 62,082 |  | 62,082 |  |  |  | 342 |
| Clarion | 200,860 |  | 111,300 | 89,560 |  |  | 930 |
| Coatesville | 352,945 |  | 30,000 | 30,000 | 30,000 30,000 |  | 1,670 |
| Koppel | 25,909 |  | 25,909 |  |  |  | 87 |
| Lehman Pike | 0 |  |  |  |  |  | 0 |
| Pocono | 150,648 |  | 75,000 | 75,648 |  |  | 777 |

PAWC-WD also provided supplemental information to the Commission that detailed its projected schedule for replacement and rehabilitation of DSIC-eligible property for each wastewater system based on the preliminary results of its condition assessment.  PAWC-WD also included a breakdown of expenditures for each type of eligible property by year and by wastewater system (district), with expenditures for combined and sanitary systems displayed separately.  PAWC-WD notes that it will include an annual update of its Condition Assessment Schedule with its subsequent AAOP filings.

Comments

No comments were received regarding the schedule for planned repair and replacement of eligible property.

Resolution

PAWC-WD notes that for work on sewer mains, it may entirely replace, or rehabilitate mains with slip lining and other methods.  Replacement is typically more expensive than rehabilitation.  It is important for Commission staff and other interested parties to understand PAWC-WD’s expenditures on sewer main work.  Therefore, PAWC-WD, beginning with its AAOP for calendar year 2020, shall include in its AAOP detailed information on the amount of sewer pipe that is replaced or rehabilitated each year.

Upon review of PAWC-WD’s Modified LTIIP, as amended, and any supplemental information filed, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code § 121.3(a)(2) by providing a schedule for planned repair and replacement of eligible property.

(3) LOCATION OF THE ELIGIBLE PROPERTY

PAWC-WD’s Position

PAWC-WD reports that it has eligible property located across the state in 3 regional locations.  PAWC-WD’s regions consist of the Central Pennsylvania region, the Northeastern Pennsylvania region and the Southeastern Pennsylvania region.  PAWC-WD provided brief summaries of each wastewater system in the regions including the types of eligible property and strategies for accelerated rehabilitation and replacement in each system.

PAWC-WD’s regions are broken down below by geographical location below.

The Central Pennsylvania region consists of:

- The Fairview North wastewater system in York County.

- The Fairview South wastewater system in York County.

- The Franklin wastewater system in Adams County.

- The McEwensville wastewater system in Northumberland County.

- The New Cumberland wastewater system in Cumberland County.

The Northeastern Pennsylvania region consists of:

- The Blue Mountain Lake (BML) wastewater system located in Monroe County.

- The Lehman Pike (LP) wastewater system serves portions of Middle Smithfield Township in Monroe County, and portions of Lehman Township in Pike County.

- The Marcel Lake (ML) wastewater system located in Pike County.

- The Pocono wastewater system in Monroe County.

- The Scranton combined sewer system.  (Formerly Scranton Sewer Authority) located in Lackawanna County.

The Southeastern Pennsylvania region consists of:

- The Coatesville wastewater system in Chester County.

- The Clarion wastewater system in Clarion County.

- The Claysville wastewater system in Washington County.

- The Koppel wastewater system in Beaver County.

- The McKeesport combined sewer system in Allegheny County.

- The Dravosburg combined sewer system in Allegheny County.

- The Duquesne combined sewer system in Allegheny County.

- The Paint-Elk wastewater system in Clarion County.

Comments

No comments were received regarding the location of eligible property.

Resolution

Upon review of PAWC-WD’s Modified LTIIP, as amended, and any supplemental information filed, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code § 121.3(a)(3) by providing a general description of the location of eligible property.

(4) REASONABLE ESTIMATES OF THE QUANTITY OF PROPERTY TO BE IMPROVED and

(5) PROJECTED ANNUAL EXPENDITURES AND MEASURES TO ENSURE THAT THE PLAN IS COST EFFECTIVE

PAWC-WD’s Position

PAWC-WD’s estimated quantities of property by year and category that are to be replaced or rehabilitated are listed in Table 4, below.  PAWC-WD in its filing, included a schedule broken down by year and system, indicating that it will replace or rehabilitate a total of 1,212 manholes, 3,451 service laterals and 15 lift stations during the remaining time period of 2020 through 2023.  PAWC-WD states that the best available information was used regarding the infrastructure needs for each wastewater system in order to compile these estimates.  However, PAWC-WD notes that actual quantities and scheduling may change depending on the outcome of sewer system evaluations or other planning studies.

Table 4 – Projected Wastewater DSIC Eligible Properties to Be Replaced / Rehabilitated for 2019 to 2023

| Year | Gravity Pipe (LF) | Manholes (ea) | Service Laterals (ea) | Lift Stations (ea) |
| --- | --- | --- | --- | --- |
| 2019 | 35,298 | 197 | 453 | 6 |
| 2020 | 62,531 | 172 | 632 | 7 |
| 2021 | 83,786 | 240 | 747 | 3 |
| 2022 | 91,038 | 303 | 888 | 2 |
| 2023 | 104,701 | 392 | 1,071 | 2 |
| McKeesport CO & Coatesville CMP |  |  |  |  |
| McKeesport | 24,044 | 55 | 100 | 0 |
| Coatesville | 14,955 | 50 | 13 | 1 |

*Service laterals listed in this table do not include any customer owned portions.

In Table 5 below, PAWC-WD’s projected annual wastewater DSIC expenditures for 2019 through 2023 are listed.  PAWC-WD maintains that these estimates are based on the quantities listed in Table 4 and recent competitively-bid prices in Pennsylvania.  PAWC-WD notes that non-regulatory wastewater DSIC investments are expenditures that exclude regulatory driven costs such as projects associated with a consent order agreement (CO) or a connection management plan (CMP).  PAWC-WD states that in future AAOP’s and other LTIIP-related filings, it will continue to distinguish between non-regulatory and regulatory investments and will separately identify expenditures for combined and sanitary systems.

Table 5 – Projected Annual Wastewater DSIC Expenditures 2019 to 2023 in millions

| Year | Non-Regulatory Investment | Regulatory |  | Total Investment |
| --- | --- | --- | --- | --- |
|  |  | McKeesport CO | Coatesville CMP |  |
| 2019 | $11.69M | $9.55M | $9.26M | $30.50M |
| 2020 | $20.07M |  |  | $20.07M |
| 2021 | $20.98M |  |  | $20.98M |
| 2022 | $20.36M |  |  | $20.36M |
| 2023 | $22.63M | $1.21M |  | $23.84M |

PAWC-WD notes that some quantities may change depending on the results of the sewer system evaluations and engineering studies.  PAWC-WD maintains that costs may vary depending on whether a replacement or rehabilitation method was selected during the final design.  For example, PAWC-WD notes that competitive bid prices for gravity replacement varied with the depth of pipe and diameter, so an average depth and diameter was assumed to generate a projected cost.  PAWC-WD states that its annual expenditures may be subject to periodic fluctuation due to larger wastewater upgrades associated with regulatory compliance, so those upgrades association with regulatory compliance have been listed separately.  PAWC-WD maintains that for all projects, the most prudent and cost-effective method will be selected.  PAWC-WD states that it uses competitive bidding to ensure all major capital projects are completed in a cost-effective manner.

PAWC-WD notes that pursuant to Ordering Paragraph 7 of the Commission’s October 26, 2017 Order at Docket No. A-2017-2606103 (2017 Order), PAWC-WD may collect a DSIC related to the McKeesport system prior to the first base rate case in which the McKeesport system’s plant-in-service is incorporated into PAWC-WD’s rate base, subject to 3 conditions.  PAWC-WD notes that though the filing of the Modified LTIIP, the first of those conditions (2017 Order, Ordering Paragraph 7(a)) is satisfied because the Modified LTIIP does not re-prioritize other existing commitments in other service areas.   The second condition (2017 Order, Ordering Paragraph 7(b)) would be met if the Modified LTIIP is approved.  The third condition (2017 Order, Ordering Paragraph 7(c)) would be met if PAWC-WD files a compliance tariff supplement filing incorporating the McKeesport service territory into PAWC-WD’s existing wastewater DSIC tariff provisions.  PAWC-WD further notes that in future LTIIP and AAOP filings, any changes in projected quantities or projected expenditures for the McKeesport system will be based on an updated assessment of the condition of the McKeesport system and will not re-prioritize existing commitments in other service areas.

PAWC-WD also notes that if in future LTIIP and AAOP filings projected quantities or projected expenditures are higher for the McKeesport system and lower for other service areas than the projections in its approved LTIIP, PAWC-WD will include an explanation why the shift was appropriate and does not re-prioritize existing commitments in other service areas.  In addition, in future water and wastewater LTIIP and AAOP filings, if projected quantities or projected expenditures are higher for systems acquired under 66 Pa. C.S. § 1329 and lower for other service areas – compared to its approved LTIIP – the Company will include an explanation why the shift was appropriate and does not re-prioritize existing commitments in other service areas.

Comments

No comments were received regarding the reasonable estimates of the quantity or expenditures of property to be improved, and cost effectiveness of the plan.

Resolution

Upon review of PAWC-WD’s Modified LTIIP, as amended, and any supplemental information filed, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code §§ 121.3(a)(4)-(5) by providing reasonable estimates of the quantity of property to be improved and the projected annual expenditures and means to finance the expenditures and ensure cost effectiveness.

(6) ACCELERATED REPLACEMENT AND MAINTAINING ADEQUATE, EFFICIENT, SAFE, RELIABLE AND REASONABLE SERVICE TO CUSTOMERS

PAWC-WD’s Position

PAWC-WD maintains that it has continuously invested in its wastewater infrastructure to maintain safe, reliable service to its customers.  PAWC-WD proposes to increase non-regulatory wastewater DSIC eligible spending from 2019 through 2023, to over $20 million annually in order to continue making necessary improvements at an accelerated pace.  PAWC-WD notes that the proposed spending for 2019 to 2023 represents a 159% increase in wastewater DSIC spending, excluding regulatory driven projects.

PAWC-WD notes that I&I has been reduced in several areas since the Wastewater DSIC rate mechanism was implemented.  However, PAWC-WD did not provide detailed information on I&I on a per system or system-wide basis.

In supplemental information filed, PAWC-WD provided information in a table that details historic annual DSIC-eligible expenditures in each district, from 2015 through 2019, and contains a summary of historic annual replacement for DSIC-eligible categories of plant for 2015 through 2018 by district.  Table 6, below, provides the overall historical expenditures.

Table 6 - Historic Annual Wastewater DSIC Expenditures in millions

* Existing WW DSIC Qualified Districts

| Year | Annual DSIC Expenditures |
| --- | --- |
| 2015 | $8.92M |
| 2016 | $5.51M |
| 2017 | $8.42M |
| 2018 | $3.86M |
| 2019 | $11.90M |

** Existing plus Future WW DSIC Qualified Districts under modified LTIIP

| Year | Annual DSIC Expenditures |
| --- | --- |
| 2015 | $8.92M |
| 2016 | $5.51M |
| 2017 | $8.42M |
| 2018 | $6.18M |
| 2019 | $39.44M |

Comments

No comments were received regarding the manner in which the infrastructure replacement will be accelerated.

Resolution

As noted on page 21, above, PAWC-WD did not provide detailed information on I&I by individual wastewater system, nor an overall baseline I&I.   It is important for Commission staff and other interested parties to understand PAWC-WD’s baseline I&I by individual system and overall system in order to monitor progress on I&I reduction.  Therefore, beginning with its AAOP for calendar year 2020, PAWC-WD shall include a baseline I&I for each system and an overall I&I baseline as of year-end 2019.  PAWC-WD shall also provide an update on the progress of the I&I reduction for each of its wastewater systems.

Upon review of PAWC-WD’s Modified LTIIP, as amended, and any supplemental information filed, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code §§ 121.3(a)(6) by providing a description of the manner in which infrastructure replacement will be accelerated and how repair, improvement, or replacement will ensure and maintain adequate, efficient, safe, reliable, and reasonable service to customers.

(7) WORKFORCE MANAGEMENT AND TRAINING PROGRAM

PAWC-WD’s Position

PAWC-WD states that to help ensure system reliability and public safety, all its wastewater DSIC eligible projects will be constructed by trained PAWC-WD staff or by pre- qualified contractors.  PAWC-WD reports that for some of its wastewater systems, its staff completes investigative work, spot repairs or lift station repairs which may be DSIC eligible.  PAWC-WD notes that its DSIC eligible projects are typically bundled together for competitive bidding to prequalified contractors in order to achieve economies of scale.

PAWC-WD notes that it utilizes a pre-qualification process to ensure all contractors are qualified to perform work in a cost-effective, safe, and reliable manner.  PAWC-WD states that it utilizes Avetta as a third-party entity to monitor contractor safety performance.  PAWC-WD maintains that the Avetta contractor prequalification process helps them certify and centralize contractor data, perform pre-project screening, and contractor pre-qualifications.  PAWC-WD states that by utilizing Avetta, it allows them to more effectively manage its risk and contractor’s performance.

PAWC-WD states that during the pre-qualification screening process, contractors are required to submit pertinent documentation, such as:

- Safety:  company policy, designated safety inspector, OSHA lost workdays and recordable incidents, OSHA violations

- Worker’s Compensation Experience Ratings (Experience Modifier)

- Staffing information

- Annual value of work and percentage of work relevant to bid project

- Work experience schedule

- Bonding capacity

- Liability Insurance coverage

- References

PAWC-WD maintains that all its construction projects performed by independent contractors are properly inspected.  PAWC-WD notes that its employees are actively engaged in the direct supervision of project inspections.  PAWC-WD adverts that the project close-out process includes a punch-list to ensure all work is completed according to contract documents.

Comments

No comments were received regarding the workforce management and training program.

Resolution

Upon review of the PAWC-WD’s Modified LTIIP, as amended, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code § 121.3(a)(7) by providing a workforce management and training program that is designed to ensure that PAWC-WD will have access to a qualified workforce to perform the work in a cost effective, safe and reliable manner.

(8) DESCRIPTION OF OUTREACH AND COORDINATION ACTIVITIES WITH OTHER UTILITIES, PENNDOT AND LOCAL GOVERNMENTS ON PLANNED PROJECTS

PAWC-WD’s Position

PAWC-WD states that the acceleration of aging infrastructure proposed in this LTIIP will lead to travel disruptions as work is performed in the right of ways of the roadways and streets across its service area.  PAWC-WD notes that local municipalities and other utilities/agencies may be planning paving projects or underground infrastructure replacement projects located in the same right-of-way as PAWC-WD’s wastewater infrastructure.  PAWC-WD notes that it recognizes that coordination with other utilities minimizes disruption and ensures that infrastructure replacement is efficient and cost effective.

PAWC-WD plans to take the following steps to reach out to customers about disturbances, and to coordinate with other utilities and the Pennsylvania Department of Transportation (PennDOT) located within the PAWC-WD service areas:

- Utilize Pennsylvania’s one-call system for design notifications, to coordinate design work with other utilities and municipalities and Coordinate PA to identify targeted areas of anticipated work planned over a two-year look ahead period.

- Maintain open communication with local municipalities to stay informed about planned utility and paving projects.

- Maintain communication with PennDOT Utility Administrators and review the letting schedule.

- Maintain communication / working relationships with other utilities operating in our service area.

- Where applicable and cost-effective, use trenchless technologies to minimize roadway disturbance.

- Prior to working within a community, issue door-to-door notifications, press releases, and / or information letters to notify those customers / community associations affected by the work.

- PAWC-WD notes that it has launched its CodeRED system, which delivers high-speed notifications to customers when water emergencies occur.  Customers enrolling in CodeRED can be contacted quickly by text, email, telephone, and the CodeRED mobile app depending on their personal preferences.  CodeRED rapidly contacts large numbers of customers about emergency situations, which include boil water advisories, main breaks, water conservation requirements and other major events impacting water service.  The system will also be used for non-urgent notification, such as planned service outages, local hydrant flushing, low-pressure events and major traffic impacts.

- Leverage areas where PAWC-WD owns both sewer and water lines to replace both simultaneously as appropriate.

Comments

No comments were received regarding the description of outreach and coordination activities with other utilities, PennDOT and local governments on planned projects.

Resolution

Upon review of PAWC-WD’s Modified LTIIP, as amended, the Commission finds that PAWC-WD’s Modified LTIIP fulfills the requirements of 52 Pa. Code § 121.3(a)(8) by providing a description of PAWC-WD’s outreach and coordination activities with other utilities, PennDOT and local governments on planned projects and roadways that may be impacted by the Modified LTIIP.

LTIIP SUMMARY

The Commission’s review of an LTIIP must determine if the LTIIP:

- Contains measures to ensure that the projected annual expenditures are cost-effective.

- Specifies the manner in which it accelerates or maintains an accelerated rate of infrastructure repair, improvement or replacement.

- Is sufficient to ensure and maintain adequate, efficient, safe, reliable and reasonable service.

- Meets the requirements of 52 Pa. Code § 121.3(a).

The utility has the burden of proof to demonstrate that its proposed LTIIP and associated expenditures are reasonable, cost effective and designed to ensure and maintain sufficient, safe, adequate, reliable and reasonable service to consumers.

The Commission has reviewed PAWC-WD’s Modified LTIIP, as amended, and any supplemental information filed.  The Commission finds that PAWC-WD has met its burden of proof by demonstrating that its Modified LTIIP contains measures to ensure that the projected annual expenditures are cost-effective, specifies the manner in which it accelerates or maintains an accelerated rate of infrastructure repair, improvement, or replacement, is sufficient to ensure and maintain adequate, safe, reliable, and reasonable service, and meets the requirements of 52 Pa. Code § 121.3(a).  Accordingly, PAWC-WD’s Modified LTIIP is approved.

The Commission finds PAWC-WD’s Modified Long-Term Infrastructure Improvement Plan and manner it was filed conforms to the requirements of Act 11 and our Regulations.  The plan, as approved herein, is designed to maintain safe, adequate and reliable service and, as such, PAWC-WD shall be required to comply with the infrastructure replacement schedule and elements of that plan; THEREFORE,

IT IS ORDERED:

1.	That the Petition of Pennsylvania-American Water Company – Wastewater Division for Approval of its Modified Long-Term Infrastructure Improvement Plan is approved, consistent with this Order.

2.	That Pennsylvania-American Water Company – Wastewater Division, pursuant to the directives in this Order and beginning with its Annual Asset Optimization Plan for calendar year 2020, shall include in its Annual Asset Optimization Plans: updated information on its pipeline materials and diameters for all of its wastewater systems; detailed information on the amount of sewer pipe that is replaced or rehabilitated each year; a baseline and update on the progress of the inflow and infiltration (I&I) reduction for each of its wastewater systems.

3.	That the proceeding at Docket No. P-2014-2431005 be closed.

BY THE COMMISSION,

Rosemary Chiavetta

Secretary

(SEAL)

# ORDER ADOPTED: April 16, 2020

# ORDER ENTERED:  April 16, 2020

Docket No. R-2013-2355276.

https://www.legis.state.pa.us/cfdocs/legis/li/uconsCheck.cfm?yr=2012&sessInd=0&act=11.

See 52 Pa. Code § 121.3.

See Ordering Paragraph No. 2.

See Ordering Paragraph No. 2.

See Ordering Paragraph No. 2.

See 52 Pa. Code § 121.4(e).

See 52 Pa. Code § 121.4(d).