|  | COMMONWEALTH OF PENNSYLVANIA PENNSYLVANIA PUBLIC UTILITY COMMISSION COMMONWEALTH KEYSTONE BUILDING 400 NORTH STREET, HARRISBURG, PA 17120 | IN REPLY PLEASE REFER TO OUR FILE |
| --- | --- | --- |

December 8, 2020

Docket No. M-2009-2094773

RICHARD G WEBSTER JR

VP - REGULATORY POLICY & STRATEGY

PECO ENERGY COMPANY

2301 MARKET STREET S15

PHILADELPHIA, PA 19103

Dick.webster@peco-energy.com

Re:	Biennial Inspection, Maintenance, Repair and Replacement Plan (2022-2023) Docket No. M-2009-2094773

Dear Mr. Webster:

On October 1, 2020, PECO Energy Company (PECO) filed its Biennial Inspection, Maintenance, Repair and Replacement Plan (Plan), pursuant to 52 Pa. Code § 57.198(a), to be made effective on January 1, 2022.

The Commission’s regulations require EDCs to file, every two years by October 1, a biennial plan for the periodic inspection, maintenance, repair, and replacement of facilities that is designed to meet reliability performance benchmarks and standards set forth in 52 Pa. Code §§ 57.191-57.197.  The Commission’s Implementation Order, entered August 13, 2009, identified PECO as one of six (6) EDCs in Compliance Group 2 to initially file their Plan by October 1, 2010, and then every two years thereafter.  The Plan must cover the two calendar years beginning 15 months after filing and remain in effect for two calendar years thereafter (January 1, 2022 through December 31, 2023).

PECO has proposed changes to its original plan, which will be discussed herein.

Plan Consistency

52 Pa. Code § 57.198(b) Plan consistency. The plan must be consistent with the National Electrical Safety Code, Codes and Practices of the Institute of Electrical and Electronic Engineers, Federal Energy Regulatory Commission Regulations, and provisions of the American National Standards Institute, Inc.

PECO’s Plan generally complies with Section 57.198(b).

Time Frames

52. Pa. Code § 57.198(c) Time frames. The plan must comply with the inspection and maintenance standards in subsection (n).  A justification for the inspection and maintenance time frames selected shall be provided, even if the time frame falls within the intervals prescribed in subsection (n).  However, an EDC may propose a plan that, for a given standard, uses intervals outside the Commission standard, provided the deviation can be justified by the EDC’s unique circumstances or a cost/benefit analysis to support an alternative approach that will still support the level of reliability required by law.

PECO has proposed modifications, discussed infra, for the following programs, or parts of programs:

- Pole loading calculations

- Distribution Transformer Inspections

Record Keeping

52 Pa. Code § 57.198(m) Recordkeeping.  An EDC shall maintain records of its inspection and maintenance activities sufficient to demonstrate compliance with its distribution facilities inspection, maintenance, repair and replacement programs as required by sub52 Pa. Code §  (n). The records shall be made available to the Commission upon request within 30 days. Examples of sufficient records include:

(1)  Date-stamped records signed by EDC staff who performed the tasks related to inspection.

(2) Maintenance, repair and replacement receipts from independent contractors showing when and what type of inspection, maintenance, repair or replacement work was done.

PECO’s plan generally complies with Section 57.198(m).

Vegetation Management

52 Pa. Code § 57.198(n)(1) Vegetation management. The Statewide minimum inspection and treatment cycle for vegetation management is between 4-8 years for distribution facilities.  An EDC shall submit a condition-based plan for vegetation management for its distribution system facilities explaining its treatment cycle.

PECO’s plan generally complies with Section 57.198(n)(1).

Pole Inspections

52 Pa. Code § 57.198(n)(2) Pole inspections. Distribution poles shall be inspected at least as often as every 10-12 years except for the new southern yellow pine creosoted utility poles which shall be initially inspected within 25 years, then within 12 years annually after the initial inspection.  Pole inspections must include:

- Drill tests at and below ground level,

- A shell test.

- Visual inspection for holes or evidence of insect infestation.

- Visual inspection for evidence of unauthorized backfilling or excavation near the pole.

- Visual inspection for signs of lightning strikes.

- A load calculation.

The Plan states that PECO will visually inspect distribution wood poles on a 10 to 12- year cycle.

PECO included a previously approved exemption from performing pole load calculations as part of pole inspections.  PECO further clarified that it will continue to assess pole strength prior to attaching non-Company facilities and that such assessments require PECO to perform pole loading calculations.

Therefore, PECO is granted exemption from performing load calculations as part of its pole inspection program.  The Plan is consistent with the previously approved Plan and complies with Section 57.198(n)(2).

Pole Inspection Failure

52 Pa. Code § 57.198(n)(3) Pole inspection failure.  If a pole fails the groundline inspection and shows dangerous conditions that are an immediate risk to public or employee safety or conditions affecting the integrity of the circuit, the pole shall be replaced within 30 days of the date of inspection.

PECO’s Plan generally complies with Section 57.198(n)(3).

Distribution Overhead Line Inspections

52 Pa. Code § 57.198(n)(4) Distribution overhead line inspections. Distribution lines shall be inspected by ground patrol a minimum of once every 1-2 years.  A visual inspection must include checking for:

- Broken insulators.

- Conditions that may adversely affect operation of the overhead transformer.

- Other conditions that may adversely affect operation of the overhead distribution line.

PECO’s Plan generally complies with Section 57.198(n)(4).

Inspection Failure

52 Pa. Code § 57.198(n)(5) Inspection failure. If critical maintenance problems are found that affect the integrity of the circuits, they shall be repaired or replaced no later than 30 days from discovery.

PECO’s Plan generally complies with Section 57.198(n)(5).

Distribution Transformer Inspections

52 Pa. Code § 57.198(n)(6) Distribution transformer inspection. Overhead distribution transformers shall be visually inspected as part of the distribution line inspection every 1-2 years.  Above-ground pad-mounted transformers shall be inspected at least as often as every 5 years and below-ground transformers shall be inspected at least as often as every 8 years.  An inspection must include checking for:

- Rust, dents or other evidence of contact.

- Leaking oil.

- Installation of fences or shrubbery that could adversely affect access to and operation of the transformer.

- Unauthorized excavation or changes in grade near the transformer.

PECO has requested a continuation of a waiver of the 5-year inspection cycle for above-ground pad-mounted transformers.  PECO has moved to an 8-year inspection cycle to coincide with the required 8-year cycle for below-ground transformers.

PECO is conditionally granted this continued exemption based on evidence it provided in 2018 that inspection results found very few problems that could lead to equipment failure and that the 5-year inspection cycle may not be more effective than the 8-year inspection cycle.  However, PECO was directed in the December 11, 2018 letter from the Commission’s Director of Technical Utility Services (TUS) approving PECO’s Plan (December 11 Letter) to report the number of above-ground pad-mounted transformer failures in its Annual Reliability Report filed pursuant to 52 Pa. Code § 57.195, beginning with its report due April of 2019, and concluding with its report due April of 2022.  As of the date of this letter, PECO appears to have not complied with this directive.  Therefore, the continuation of this waiver is contingent upon PECO filing a report with TUS indicating the number of above-ground pad-mount transformer failures in calendar years 2018 and 2019.  PECO is directed to file this report within thirty (30) days from the date of this letter.  PECO is also hereby directed to further abide by the directives in the December 11 Letter.

Contingent upon PECO’s compliance with the directives above, PECO’s Plan generally complies with Section 57.198(n)(6).

Recloser Inspections

52 Pa. Code § 57.198(n)(7) Recloser inspections. Three-phase reclosers shall be inspected on a cycle of 8 years or less.  Single-phase reclosers shall be inspected as part of the EDC’s individual distribution line inspection plan.

PECO’s Plan generally complies with Section 57.198(n)(7).

Substation Inspections

52 Pa. Code § 57.198(n)(8) Substation inspections. Substation equipment, structures and hardware shall be inspected on a cycle of 5 weeks or less.

PECO’s Plan generally complies with Section 57.198(n)(8).  However, PECO’s Plan includes a 25% grace period for substation inspections performed on a 5-week cycle or less.  This could increase the maximum 5-week inspection cycle by up to 8 days.  This provision was previously granted and the 25% grace period has not appeared to adversely affect reliability.  In order to ensure that PECO is consistently meeting the intent of Section 57.198(n)(8), PECO is directed to report to TUS the number of substation inspections in calendar years 2018 and 2019 that were performed during the grace period.  PECO is directed to file this information within thirty (30) days of the date of this letter and PECO may include this information with its pad-mount above-ground transformer report required, above.

Conclusion

Upon review of PECO Biennial Inspection, Maintenance, Repair and Replacement Plan filed on October 1, 2020, it appears that the filing generally complies to the requirements of 52 Pa. Code § 57.198 and is accepted.  Furthermore, PECO’s requested waiver for pole loading calculations is approved and PECO’s requested waiver for pad-mount above-ground transformers is conditionally approved, pursuant to the directives in this letter.  These approvals are contingent upon the possibility that subsequent audits, reviews, and inquiries, in any Commission proceeding, may be conducted pursuant to 52 Pa. Code § 57.197(a).

This plan must remain in effect for two calendar years, beginning January 1, 2022.  PECO may, however, request Commission approval of subsequent revisions to its approved Plan, in accordance with 52 Pa. Code § 57.198(l).  Revisions must be submitted to the Commission as an addendum to PECO quarterly reliability report filed pursuant to § 57.195, including prospective and past revisions to its Plan and a justification for the revisions.

If you are dissatisfied with the resolution of this matter, you may, as set forth in 52 Pa. Code § 5.44, file a petition with the Commission within twenty (20) days after the date of this letter.  Please direct any questions regarding this filing to John Van Zant, Reliability and Emergency Preparedness Supervisor, Bureau of Technical Utility Services at (717) 773-7380, or jvanvant@pa.gov.

Sincerely,

Rosemary Chiavetta

Secretary

cc:	Amy Neufeld, PECO Energy Company, amy.neufeld@exeloncorp.com

Kriss Brown, LAW

John Van Zant, TUS

Dan Searfoorce, TUS

Brent Killian, BIE