|  | PENNSYLVANIA PUBLIC UTILITY COMMISSION Harrisburg, PA 17120 |  |
| --- | --- | --- |

|  | Public Meeting held August 5, 2021 |
| --- | --- |
| Commissioners Present: |  |

| Gladys Brown Dutrieuille, Chairman |  |  |
| --- | --- | --- |
| David W. Sweet, Vice Chairman John F. Coleman, Jr. |  |  |
| Ralph V. Yanora |  |  |
| Letter of Notification of PPL Electric Utilities Corporation for approval to reconfigure and reconstruct the Montour-Milton 230 kV Transmission Line and the Milton-Sunbury 230 kV Transmission Line and to relocate approximately one-mile of the Montour-Columbia 230 kV Transmission Line located in Montour, Northumberland, Snyder, and Union Counties, Pennsylvania | Docket Number: A-2021-3024033 |

ORDER

BY THE COMMISSION:

On February 5, 2021, PPL Electric Utilities Corporation (PPL Electric), Utility Code 110500, filed a Letter of Notification (LON) pursuant to 52 Pa. Code § 57.72(d)(1)(i) of the Pennsylvania Public Utility Commission’s (Commission) transmission line siting regulation.  For the reasons expressed in this Order, the LON is approved.

Copies of the LON were served in accordance with Section 57.72(d)(3) and 57.74(b) & (c), 52 Pa. Code §§ 57.72(d)(3), 57.74(b) & (c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Montour, Northumberland, Snyder, and Union County Commissioners, Borough of Shamokin Dam, and Liberty, Derry, Point, East Chillisquaque, West Chillisquaque, Monroe, and Union Townships, et al.  No protests were filed.  No hearings were held.

PPL Electric requests approval to reconfigure and reconstruct the Montour-Milton 230 kV Transmission Line (Montour-Milton) and the Milton-Sunbury 230 kV Transmission Line (Milton-Sunbury) and to relocate approximately one-mile of the Montour-Columbia 230 kV Transmission Line (Montour-Columbia) located in Montour, Northumberland, Snyder, and Union Counties, Pennsylvania.  The lines to be rebuilt include approximately 10.7 miles of the Montour-Milton line and approximately 10.5 miles of the Milton-Sunbury transmission line.

PPL Electric states that the reconstruction of the Montour-Milton and Milton-Sunbury lines is necessary to resolve significant asset health condition concerns across the Montour-Milton and Milton Sunbury transmission lines associated with the presence of pack-out rust in the existing COR-TEN steel lattice towers, to resolve projected thermal violations in the affected region, and to resolve generator stability concerns.  Application ¶9.

PPL Electric avers that independent field investigations and assessments were conducted in 2013 (2013 Assessment), 2019, and 2020 by separate third party entities and revealed that the aging Montour-Milton and Milton-Sunbury transmission line facilities are showing signs of significant deterioration.  PPL Electric also avers that based on the results of these assessments, the issue with COR-TEN lattice towers has accelerated the deterioration of these structures and has brought the assets to the end of their service life much sooner than would have been anticipated.  PPL Electric further avers that at roughly 50 years of age, the COR-TEN lattice towers that comprise the Montour-Milton and Milton Sunbury 230 kV lines have exceeded their useful life and can no longer be relied upon to safely operate as designed.  Lastly, PPL Electric avers that the loss of the Montour-Milton or Milton-Sunbury transmission lines would result in a 105 MW load drop and loss of service to approximately 14,000 customers including several critical customers.

Application ¶¶14, 16, 20, & 22-23.

PPL Electric states that the Montour-Milton transmission line was constructed in 1971 and includes 63 weathering-steel COR-TEN steel lattice structures spanning approximately 10.7 miles of the approximately 12.6 miles of original construction.  The Milton-Sunbury transmission line was originally constructed in 1969 and has 68 weathering-steel COR-TEN lattice structures spanning approximately 10.5 miles.  PPL Electric states that COR-TEN lattice towers were commonly installed by the industry during this time because it was believed that the corrosion-resistant properties of weathering-steel would reduce future maintenance needs and costs.  PPL Electric further states that these towers had an expected service life of approximately 75 years at the time they were installed.  Application ¶13.

PPL Electric avers that in 2013, it hired a third-party contractor to perform an assessment of the Montour-Milton and Milton-Sunbury transmission lines under a steel structure capital maintenance program.  PPL Electric avers that the assessment identified that 126 of 131 structures had one or more structure legs that rated poor or very poor.  PPL Electric further avers that of those 126 structures, 25 had one or more structure legs that were identified as “priority”, requiring immediate attention.  Application ¶14.

PPL Electric submits that the asset health concerns discovered by the 2013 Assessment were heightened by the discovery of pack-out rust in the section joints of the subject COR-TEN lattice towers.  PPL Electric also submits that when the presence of

pack-out rust becomes too severe, it can deform steel members and connecting hardware, it can also shear off bolts, cause loss of structural integrity, cause members to disconnect from the tower, and even result in tower failure.  PPL Electric further submits that this now well-known inherent problem with COR-TEN steel is also being seen in other infrastructure where two pieces of COR-TEN steel overlap at joints, such as those present on lattice towers.  Application ¶15.

PPL Electric states that the accelerated deterioration of the asset health of the

COR-TEN lattice towers has been further corroborated by a recent study prepared by Osmose, in November 2020.  PPL States that Osmose was contracted to perform a condition assessment on the Milton-Sunbury and Montour-Milton transmission lines.  The sample set for the assessment consisted of a random selection of 41 of the 131 structures on these lines, which would represent a statistically significant sample set.  PPL Electric states that of the structures evaluated, over 80% were determined to have a condition rating of “Severe,” which indicates that greater than 50% of the existing structure’s joints contain pack-out rust.  PPL Electric further states that the majority of pack rust observed on each structure was found in the lower sections of the post leg where horizontal and diagonal members are bolted to the post leg.  Application ¶19 and Attachment 1, pg. 11.

PPL Electric states that the Montour-Milton-Sunbury Project consists of removing the existing COR-TEN transmission structures and rebuilding the Montour-Milton and Milton-Sunbury lines as double-circuit 230 kV transmission lines.  PPL Electric also states that as a result of the Montour-Milton-Sunbury Project, the Montour-Columbia 230kV Transmission Line that is currently collocated with the Montour-Milton line for approximately one mile will be relocated and connected into the Montour Substation.  The existing Montour-Milton transmission line will be redesignated as the Montour-Milton #1 230 kV Transmission Line and the additional 230 kV circuit on this section of the line will be designated as the Montour-Milton #2 230 kV Transmission Line and will terminate at the Milton 230-69 kV Substation, and the Montour 230 kV Switchyard.  PPL Electric further states that the existing Milton-Sunbury transmission line will be redesignated as the

Milton-Sunbury #1 230 kV Transmission Line and will be terminated at both the Milton 230-69 kV and Sunbury substations.  PPL Electric also states the existing Sunbury-Milton 69 kV line will be retired and the additional 230 kV circuit between the Sunbury and Milton substations will be designated as the Milton-Sunbury #2 230 kV Transmission Line.

Application ¶¶33-35.

PPL Electric states that in addition to addressing the asset health issues associated with the deterioration of COR-TEN lattice towers, the Montour-Milton-Sunbury Project is necessary to address thermal overload and generator stability issues by the addition of a second 230 kV circuit to the Montour-Milton and Milton-Sunbury transmission lines.  Application ¶36.

PPL Electric avers that its Susquehanna Region has excess generation, and that this excess generation and the need to transmit it elsewhere on the bulk 230 kV transmission system has created operational challenges under certain conditions.  PPL Electric avers that a three-phase fault on the double circuit Montour-Susquehanna T10 230 kV and Montour-Susquehanna 230 kV Transmission Line under light load conditions will cause generator instability leading to the loss of approximately 2,400 MW of generation.  PPL Electric further avers that tripping of these plants along with the underlying contingencies causing these unit trips will reduce the system operating margin and limit the transmission system’s ability to recover from the next contingency.  Application ¶¶27-28.

PPL Electric states that its planning analysis also shows that if the Montour-Milton-Sunbury Project is not completed, a thermal violation will occur on the Montour-Milton line under the PJM generator deliverability test.  PPL Electric performed PJM Interconnection, LLC’s (PJM) generator deliverability analysis using the 2025 Regional Transmission Expansion Plan (RTEP) summer peak case and found that the Montour-Milton transmission line will be overloaded to 104% of its summer emergency rating for the loss of the double circuit Saegers-Elimsport 230 kV Transmission Line and Saegers-Clinton 230 kV Transmission Line.  Application ¶30.

PPL Electric avers that in January 2016, it proposed supplemental project s1106 to build a new 500-230 kV substation to address the above-mentioned issue.  In early, 2020 PPL Electric identified a less costly alternative to solve the stability problem.  The alternative was proposed to PJM stakeholders at the March 2020 Transmission Expansion Advisory Committee meeting.  Lastly, PPL Electric avers that the proposed changes were included by PJM staff in the final RTEP.  Application ¶29.

PPL Electric submits that when it proposed supplemental project s1106 in 2016 there was no thermal violation on the Montour-Milton line.  However, in the previous five years, approximately 2,750 MW of new generation has been added in the area.  PPL Electric also submits that the presence of s1106 in the RTEP model has prevented a thermal overload on the Montour-Milton transmission line caused by the addition of new generation.  PPL Electric further submits that while s1106 did not initially contemplate the rebuild proposed by the Montour-Milton-Sunbury Project, PPL Electric proposed to address the subject thermal violation as a part of the Montour-Milton-Sunbury Project in order to address multiple needs at once, rather than undertaking separate projects at an additional cost.  Application ¶¶31-32.

PPL Electric avers that in order to resolve the identified COR-TEN lattice tower health conditions, thermal violation, and generator stability issues, it proposes to rebuild the existing Montour-Milton and the Milton-Sunbury transmission lines as double-circuit 230kV lines.  PPL Electric also avers that the addition of the second 230 kV circuit on the Montour-Milton line, and the operation of it and the Milton-Sunbury line as double-circuit 230 kV transmission lines as a part of the Montour-Milton-Sunbury Project, are required to address the generator stability and thermal violation.  PPL Electric notes that the Montour-Milton-Sunbury Project replaces all 131 COR-TEN lattice structures as well as the conductor for the Montour-Milton and the Milton-Sunbury transmission lines.

Application ¶33.

PPL Electric avers that to facilitate rebuilding the Montour-Milton line to double-circuit 230 kV operation, the sections of the Montour-Columbia and Montour-Millville

69 kV transmission lines that are presently collocated with the Montour-Milton line will be re-routed.  PPL Electric further avers that a one-mile section of the Montour-Columbia line will be rebuilt in existing right-of-way (ROW) across the Montour Power Plant property and re-terminated in the southeastern part of the property.  Application Attachment 2, pg. 4.

PPL Electric states that, in addition to rebuilding the Montour-Milton and Milton-Sunbury transmission lines, it considered two alternative solutions, structure replacement and the addition of the Catawissa Substation, and structure restoration and the addition of the Catawissa Substation.  PPL Electric states that the estimated total cost of ownership over a 45-year period for the two alternative solutions is approximately $385.8 million and $394.2 million, respectively.  Accordingly, PPL Electric submits that the two alternatives were rejected for a solution which addresses the reliability risk and aging infrastructure in a cost-effective manner.  PPL Electric further states that the 45-year cost of the chosen solution is approximately $277.5 million.  Application Attachment 1, Section 5.0.

PPL Electric states that it will remove the 131 existing COR-TEN structures and install 111 new double circuit steel monopole and 2-pole structures.  The existing structures range from approximately 61 feet in height to 215 feet in height and the new steel structures will range from approximately 100 feet in height to 210 feet in height.  The new poles will be self-supported, either directly embedded or on concrete caisson foundations.  The new transmission structures are anticipated to have a service life of approximately 75 years.  Additionally, PPL Electric states that relocation of the Montour-Columbia includes the construction of 7 new double circuit steel monopoles. Application Attachment 2, Table 2-4, Table 2-8, Attachment 2, pages 4-5, and PPL Electric Data Request Response No. 13.

In its filing, PPL Electric states that the Montour-Milton-Sunbury Project has been designed and will be built within a 150-foot-wide existing ROW of the Montour-Milton and Milton-Sunbury transmission lines.  PPL Electric also states that the new structures will be located near the existing structures and that in instances where the structures will be relocated, the proposed locations have been discussed with the property owners who did not object.  Application ¶¶41-42.

PPL Electric asserts that the Montour-Milton-Sunbury Project will be designed, constructed, operated and maintained in a manner that meets or surpasses all applicable PPL Electric and National Electrical Safety Code minimum standards and all applicable legal requirements.  Application ¶39.

PPL Electric states that the total estimated cost for the Montour-Milton-Sunbury Project is approximately $89.9 million and will be paid for by PPL Electric.  Construction of the project is anticipated to commence in September 2021 with a proposed in-service date of July 2023.  Application Attachment 1, Pgs. 2-3.

Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

- An HV line which is proposed to be located entirely on an existing

transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the

right-of-way.

(ii)	An HV line which is proposed to be located entirely within a public road.

- An HV line which is proposed to be located entirely within applicant’s existing

transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

- A line for which the voltage is proposed to be increased above its present

levels so long as the size, character, design, or configuration of the proposed

HV line does not substantially alter the right-of-way.

(v)	An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way

- An HV line having a proposed route of 2 miles or less.

52 Pa. Code § 57.72(d).

We agree with PPL Electric that the formal PPL Electric Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(i) because the Montour-Milton-Sunbury Project reconfigures and reconstructs the Montour-Milton, Milton-Sunbury, and Montour-Columbia transmission lines in such a manner that it does not substantially alter the existing ROW.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.

We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

- That the Letter of Notification filed by PPL Electric Utilities Corporation for approval to reconfigure and reconstruct the Montour-Milton 230 kV Transmission Line and the Milton-Sunbury 230 kV Transmission Line and to relocate approximately one-mile of the Montour-Columbia 230 kV Transmission Line located in Montour, Northumberland, Snyder, and Union Counties, Pennsylvania, is hereby approved.

- That upon completion of the subject project, PPL Electric Utilities Corporation shall file the final project cost with the Commission.

- That upon completion of Ordering Paragraph 2, this proceeding at Docket

No. A-2021-3024033 be closed.

BY THE COMMISSION,

Rosemary Chiavetta

Secretary

ORDER ADOPTED: August 5, 2021

ORDER ENTERED: August 5, 2021