	
	PENNSYLVANIA

PUBLIC UTILITY COMMISSION

Harrisburg, PA  17120
	


	
	Public Meeting held October 7, 2021

	Commissioners Present:
	


	Gladys Brown Dutrieuille, Chairman
	

	John F. Coleman, Jr.
	

	Ralph V. Yanora 
	

	
	

	
	

	Letter of Notification of PECO Energy Company for approval to Remove and Replace an existing Transmission Line Structure in Plymouth Township, Montgomery County, Pennsylvania


	Docket Number:

A-2021-3027998


ORDER

BY THE COMMISSION:

On August 18, 2021, PECO Energy Company (PECO), Utility Code 110550, filed a Letter of Notification (LON) pursuant to 52 Pa. Code § 57.72(d)(1)(vi) of the Pennsylvania Public Utility Commission’s (Commission) transmission line siting regulation.  For the reasons expressed in this Order, the LON is approved.

Copies of the LON were served in accordance with Section 57.72(d)(3) and 57.74(b) & (c), 52 Pa. Code §§ 57.72(d)(3), 57.74(b) & (c), on the PA Department of Transportation, PA Department of Environmental Protection, PA Historical and Museum Commission, Montgomery County Commissioners, and Plymouth Township, et al.  No protests were filed.  No hearings were held.


PECO requests approval to remove and replace an existing transmission line structure in Plymouth Township, Montgomery County, Pennsylvania.  PECO states that the structure to be replaced is located on its 130-35 138kV Transmission Line which spans from Plymouth Meeting Substation to Bryn Mawr Substation.  The structure is located inside PECO’s wood pole storage yard at its facility on Gallagher Road.
PECO avers that the existing structure has reached the end of its reliable life.  The structure is comprised of three wood poles which have significant longitudinal cracking, bird holes, and rot.  PECO further avers that the structure is approximately 57 years in age and has an anticipated service life of approximately 50 years.  Application ¶8 and PECO Data Request Response No. 2.

PECO states that replacing the transmission line structure (Proposed Project) consists of removing the existing structure and installing one new steel monopole.  The new structure will be located approximately 25 feet north of the existing structure and will be approximately 60 feet in height.  PECO further states that the existing structure to be removed is approximately 61 feet in height.  Lastly, PECO states that the Proposed Project will be constructed on approximately 0.15 miles of existing right-of-way that is approximately 315 feet in width.  Application ¶9; Attachment 3, pg 2; and PECO Data Request Response No. 5.
PECO submits that the Proposed Project will be designed, constructed, operated, and maintained in a manner that meets or exceeds the requirements specified in the National Electrical Safety Code, Occupational Safety and Health Administration safety standards, and all applicable legal requirements.  Application ¶14.
PECO states that the total estimated cost for the Proposed Project is approximately $500,000, and that all costs will be paid for by PECO.  Construction of the Proposed Project is anticipated to commence November 11, 2021, with a proposed in-service date of November 22, 2021.  Application ¶¶11-12 and PECO Data Request Response No. 3.
Section 57.72 authorizes the abbreviated LON siting application process in lieu of an application for the following:

(i) An HV line which is proposed to be located entirely on an existing 

Transmission line right-of-way, so long as the size, character, design, or

configuration of the proposed HV line does not substantially alter the 

right-of-way.

(ii)
An HV line which is proposed to be located entirely within a public road.

(iii) An HV line which is proposed to be located entirely within applicant’s existing

transmission line right-of-way and the property of the sole customer to be served by the line, so long as the size, character, design, or configuration of the proposed HV line does not substantially alter the right-of-way.

(iv) A line for which the voltage is proposed to be increased above its present 

levels so long as the size, character, design, or configuration of the proposed 

HV line does not substantially alter the right-of-way. 

(v) An HV line which is to be reconductored or reconstructed so long as the size, character, design or configuration of the proposed HV line does not substantially alter the right-of-way.

          (vi) An HV line having a proposed route of 2 miles or less.

52 Pa. Code § 57.72(d).

We agree with PECO that the formal PECO Letter of Notification and manner in which it was filed conforms to the requirements of 52 Pa. Code § 57.72(d)(1)(vi) because the Proposed Project will remove and replace an existing transmission line structure along a section of the 130-35 Transmission Line that is less than 2 miles in length.  Moreover, the Commission has reviewed the filing and does not find it to be inconsistent with the applicable law or Commission policy regarding transmission line siting and, therefore, to be in the public interest.  

We also note that our approval of the Letter of Notification does not address the issues of accounting treatment, and cost recovery; THEREFORE,

IT IS ORDERED:

1. That the Letter of Notification filed by the PECO Energy Company, for approval to remove and replace an existing transmission line structure in Plymouth Township, Montgomery County, Pennsylvania, is hereby approved.  

2. That upon completion of the subject project, PECO Energy Company shall submit the final project cost to the Commission.

3. That upon completion of Ordering Paragraph 2, this proceeding at Docket 
No. A-2021-3027998 be closed. 

[image: image1.png]


BY THE COMMISSION,

Rosemary Chiavetta

Secretary

ORDER ADOPTED: October 7, 2021
ORDER ENTERED: October 7, 2021

