|  | COMMONWEALTH OF PENNSYLVANIA PENNSYLVANIA PUBLIC UTILITY COMMISSION 400 NORTH STREET, HARRISBURG, PA 17120 | IN REPLY PLEASE REFER TO OUR FILE |
| --- | --- | --- |

December 21, 2021

Docket No. M-2009-2094773

TORI GIESLER

ATTORNEY, FIRST ENERGY

2800 POTTSVILLE PIKE

PO BOX 16001

READING, PA 19612-6001

tgiesler@firstenergycorp.com

Re:	Metropolitan Edison Company’s Biennial Inspection, Maintenance, Repair and Replacement Plan (2023 through 2024) Docket No. M-2009-2094773

Dear Ms. Giesler:

On October 1, 2021, Metropolitan Edison Company (“Met-Ed”) filed its Biennial Inspection, Maintenance, Repair and Replacement Plan (“Plan”), pursuant to 52 Pa. Code § 57.198(a), to be made effective on January 1, 2023.

The Commission’s regulations require EDCs to file, every two years by October 1, a biennial plan for the periodic inspection, maintenance, repair, and replacement of facilities that is designed to meet reliability performance benchmarks and standards set forth in 52 Pa. Code §§ 57.191-57.197.  The Commission’s Implementation Order, entered August 13, 2009, identified Met-Ed as one of five EDCs in Compliance Group 1 which must file their seventh biennial Plan by October 1, 2021.  The Plan must cover the two calendar years beginning 15 months after filing and remain in effect for two calendar years thereafter (January 1, 2023, through December 31, 2024).

Met-Ed’s I&M Plan for 2023 and 2024 is consistent with its previously approved plan for 2021 through 2022 and proposes no substantive changes.

Plan Consistency

52 Pa. Code § 57.198(b) Plan consistency.  The plan must be consistent with the National Electrical Safety Code, Codes and Practices of the Institute of Electrical and Electronic Engineers, Federal Energy Regulatory Commission Regulations, and provisions of the American National Standards Institute, Inc.

Met-Ed’s Plan states it complies with 52 Pa. Code § 57.198(b) requirements.

Time Frames

52. Pa. Code § 57.198(c) Time frames. The plan must comply with the inspection and maintenance standards in subsection (n).  A justification for the inspection and maintenance time frames selected shall be provided, even if the time frame falls within the intervals prescribed in subsection (n).  However, an EDC may propose a plan that, for a given standard, uses intervals outside the Commission standard, provided the deviation can be justified by the EDC’s unique circumstances or a cost/benefit analysis to support an alternative approach that will still support the level of reliability required by law.

Met-Ed continues previously approved modifications, discussed infra, for the following programs, or parts of programs:

- Pole inspections

- Distribution overhead line inspection interval

- Distribution overhead transformer inspection interval

Record Keeping

52 Pa. Code § 57.198(m) Recordkeeping.  An EDC shall maintain records of its inspection and maintenance activities sufficient to demonstrate compliance with its distribution facilities inspection, maintenance, repair, and replacement programs as required by subsection (n). The records shall be made available to the Commission upon request within 30 days. Examples of sufficient records include:

(1)  Date-stamped records signed by EDC staff who performed the tasks related to inspection.

(2) Maintenance, repair, and replacement receipts from independent contractors showing when and what type of inspection, maintenance, repair or replacement work was done.

Met-Ed’s Plan states it complies with 52 Pa. Code § 57.198(m) requirement.

Vegetation Management

52 Pa. Code § 57.198(n)(1) Vegetation management.  The Statewide minimum inspection and treatment cycle for vegetation management is between 4-8 years for distribution facilities.  An EDC shall submit a condition-based plan for vegetation management for its distribution system facilities explaining its treatment cycle.

The Plan includes three vegetation management methods for promoting safe and reliable operation of their distribution system. The first method is the Standard Specification, which provides vegetation to be pruned to achieve a five (5) year cycle for clearance.  This includes: removal of selected incompatible trees within the clearing zone corridor; removal of certain defective limbs that are overhanging primary conductors; controlling selected incompatible brush mechanically and/or using herbicide; and removal of off-corridor priority trees that are dead, dying, diseased, and leaning or significantly encroaching the corridor.  The Standard Specification is used on portions of circuits that experience high customer interruption minutes due to vegetation-caused outages.

Met-Ed utilizes the second method, Enhanced Specification, on targeted circuit locations that experience high customer interruption minutes due to vegetation-caused outages.  The Enhanced Specification includes the methods from the Standard Specification plus the removal of certain healthy limbs that overhang primary conductors.

Met-Ed utilizes the third method, Inspect/Maintain, for portions of circuits that have not experienced significant reliability issues due to vegetation-caused outages. The process involves inspection of vegetation around the circuits and removal of vegetation that has the potential for interference with conductors. The Inspect/Maintain process targets selective vegetation removal on a cycle which will not exceed eight (8) years.

Met-Ed’s Plan generally complies with section 57.198(n)(1).

Pole Inspections

52 Pa. Code § 57.198(n)(2) Pole inspections.  Distribution poles shall be inspected at least as often as every 10-12 years except for the new southern yellow pine creosoted utility poles which shall be initially inspected within 25 years, then within 12 years annually after the initial inspection.  Pole inspections must include:

- Drill tests at and below ground level,

- A shell test.

- Visual inspection for holes or evidence of insect infestation.

- Visual inspection for evidence of unauthorized backfilling or excavation near the pole.

- Visual inspection for signs of lightning strikes.

- A load calculation.

The Plan states that Met-Ed will visually inspect distribution wood poles on a 12-year cycle.  The preventative maintenance inspection for wood poles will include a visual inspection as well as hammer-sounding as needed.  The inspection consists of the recording of abnormal conditions from the groundline to the top of the pole, including damage (broken or leaning), equipment (crossarms, insulators, conductors, oil leaking), and testing for decayed internal wood.  Poles showing incipient decay or poles that are 35 years old or older will be bored to further assess the condition of the pole.

Met-Ed included a previously approved exemption from performing pole load calculations as part of pole inspections.

Met-Ed’s Plan generally complies with Section 57.198(n)(2).

Pole Inspection Failure

52 Pa. Code § 57.198(n)(3) Pole inspection failure.  If a pole fails the groundline inspection and shows dangerous conditions that are an immediate risk to public or employee safety or conditions affecting the integrity of the circuit, the pole shall be replaced within 30 days of the date of inspection.

The Plan states that wood poles and supporting structures with recorded defects that Met-Ed could reasonably expect to endanger life or property will be repaired or replaced within 30 days.  All remaining deficiencies will be evaluated and prioritized on a case-by-case basis.

Met-Ed’s Plan generally complies with Section 57.198(n)(3).

Distribution Overhead Line Inspections

52 Pa. Code § 57.198(n)(4) Distribution overhead line inspections.  Distribution lines shall be inspected by ground patrol a minimum of once every 1-2 years.  A visual inspection must include checking for:

- Broken insulators.

- Conditions that may adversely affect operation of the overhead transformer.

- Other conditions that may adversely affect operation of the overhead distribution line.

Met-Ed’s Plan includes a previously approved exemption for a five (5) year inspection cycle, rather than the required one to two (1-2) year cycle.  During this inspection cycle, Met-Ed has added switches and sectionalizers to their overhead line inspection plan, which is an addition from its previously approved plan.

Met-Ed’s Plan generally complies with section 57.198(n)(4).

Inspection Failure

52 Pa. Code § 57.198(n)(5) Inspection failure.  If critical maintenance problems are found that affect the integrity of the circuits, they shall be repaired or replaced no later than 30 days from discovery.

The Plan states that supporting structures with recorded defects that Met-Ed could reasonably expect to affect the integrity of the circuit shall be repaired/replaced within 30 days.  All remaining deficiencies will be evaluated and prioritized on a case-by-case basis.

Met-Ed’s Plan generally complies with Section 57.198(n)(5).

Distribution Transformer Inspections

52 Pa. Code § 57.198(n)(6) Distribution transformer inspection.  Overhead distribution transformers shall be visually inspected as part of the distribution line inspection every 1-2 years.  Above-ground pad-mounted transformers shall be inspected at least as often as every 5 years and below-ground transformers shall be inspected at least as often as every 8 years.  An inspection must include checking for:

- Rust, dents, or other evidence of contact.

- Leaking oil.

- Installation of fences or shrubbery that could adversely affect access to and operation of the transformer.

- Unauthorized excavation or changes in grade near the transformer.

Met-Ed’s Plan includes a previously approved exemption for a five (5) year inspection cycle for overhead transformers, consistent with their overhead line inspection cycle, instead of the required one to two (1-2) year cycle. Met-Ed will inspect above-ground pad-mounted transformers on a five (5) year cycle and below-ground transformers on an eight (8) year cycle.

Met-Ed’s Plan generally complies with section 57.198(n)(6).

Recloser Inspections

52 Pa. Code § 57.198(n)(7) Recloser inspections.  Three-phase reclosers shall be inspected on a cycle of 8 years or less.  Single-phase reclosers shall be inspected as part of the EDC’s individual distribution line inspection plan.

The Plan states that Met-Ed visually inspects distribution line reclosers annually and this practice is the same for all FirstEnergy companies.

Met-Ed’s Plan generally complies with section 57.198(n)(7).

Substation Inspections

52 Pa. Code § 57.198(n)(8) Substation inspections. Substation equipment, structures and hardware shall be inspected on a cycle of 5 weeks or less.

Met-Ed’s Plan includes inspections on monthly, quarterly, and biannual intervals. Safety and security inspections are conducted monthly; readings of currents, etc. are performed quarterly; and a more comprehensive inspection of substation equipment are performed biannually.  This Plan is consistent with all FirstEnergy companies.

Met-Ed’s Plan generally complies with section 57.198(n)(8).

Conclusion

Upon review of Met-Ed’s Biennial Inspection, Maintenance, Repair and Replacement Plan filed on October 1, 2021, it appears that the filing generally complies to the requirements of 52 Pa. Code § 57.198.  Furthermore, as discussed supra, the previously approved exemptions requested by Met-Ed may continue.  These approvals are contingent upon the possibility that subsequent audits, reviews, and inquiries, in any Commission proceeding, may be conducted pursuant to 52 Pa. Code § 57.197(a).

This plan must remain in effect for two calendar years, beginning January 1, 2023, through December 31, 2024.  Met-Ed may however, request Commission approval of subsequent revisions to its approved Plan, in accordance with 52 Pa. Code § 57.198(l).  Revisions must be submitted to the Commission as an addendum to Met-Ed’s quarterly reliability report filed pursuant to § 57.195, including prospective and past revisions to its Plan and a justification for the revisions.

If you are dissatisfied with the resolution of this matter, you may, as set forth in 52 Pa. Code § 5.44, file a petition with the Commission within twenty (20) days after the date of this letter.  Please direct any questions regarding this filing to Harry R. Bidelspach, Sr., Electrical Reliability Engineer, Bureau of Technical Utility Services at (717) 425-7401, or hbidelspac@pa.gov

Sincerely,

Rosemary Chiavetta

Secretary

cc:	Kriss Brown, LAW

John Van Zant, TUS

Dan Searfoorce, TUS

Harry Bidelspach, TUS

Brent Killian, BIE

Scott R. Wyman, FirstEnergy, wymans@firstenergycorp.com